## IO Allocation
Tag | IO Type | Cable | Cable Size | Pair | IO Group | Segregation | Row Kind | Controller | System Cabinet | Marshalling Cabinet | CIOC | Baseplate | Slot | CHARM Address | CHARM Type | Terminal Block | Status | TQ Ref | Source
10-HS-1705A | DI | CBL-0088 | 24 | 1 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 1 | 001-CBP-1-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):166
10-XY-1706A | DO | CBL-0088 | 24 | 2 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 2 | 001-CBP-1-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1961
10-LT-1707A | AI | CBL-0088 | 24 | 3 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 3 | 001-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1086
10-XV-1708A | DO-SOV | CBL-0088 | 24 | 4 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 4 | 001-CBP-1-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):917
10-LT-1709A | AI | CBL-0088 | 24 | 5 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 5 | 001-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1730
10-XV-1710A | DO-SOV | CBL-0088 | 24 | 6 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 6 | 001-CBP-1-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):461
10-TT-1711A | AI | CBL-0088 | 24 | 7 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 7 | 001-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):199
10-PT-1712A | AI | CBL-0088 | 24 | 8 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 8 | 001-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1411
10-LV-1713A | AO | CBL-0088 | 24 | 9 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 9 | 001-CBP-1-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1459
10-PT-1714A | AI | CBL-0088 | 24 | 10 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 10 | 001-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1619
10-ZS-1715A | DI | CBL-0088 | 24 | 11 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 11 | 001-CBP-1-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1350
10-FV-1716A | AO | CBL-0088 | 24 | 12 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-1 | 12 | 001-CBP-1-12 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):931
10-PT-1717A | AI | CBL-0088 | 24 | 13 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 1 | 001-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):805
10-FV-1718A | AO | CBL-0088 | 24 | 14 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 2 | 001-CBP-2-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1063
10-FT-1719A | AI | CBL-0088 | 24 | 15 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 3 | 001-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1077
10-HN-1720A | DO-HORN | CBL-0088 | 24 | 16 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 4 | 001-CBP-2-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1758
10-ZS-1721A | DI | CBL-0088 | 24 | 17 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 5 | 001-CBP-2-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1457
10-PV-1722A | AO | CBL-0088 | 24 | 18 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 6 | 001-CBP-2-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):477
10-FT-1723A | AI | CBL-0088 | 24 | 19 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 7 | 001-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):438
10-LT-1724A | AI | CBL-0088 | 24 | 20 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 8 | 001-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1995
|  | CBL-0088 | 24 | 21 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 9 | 001-CBP-2-09 |  |  | Spare
|  | CBL-0088 | 24 | 22 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 10 | 001-CBP-2-10 |  |  | Spare
|  | CBL-0088 | 24 | 23 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 11 | 001-CBP-2-11 |  |  | Spare
|  | CBL-0088 | 24 | 24 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-2 | 12 | 001-CBP-2-12 |  |  | Spare
10-ZS-2130A | DI | CBL-0132 | 24 | 1 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 1 | 001-CBP-3-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1910
10-TT-2131A | AI | CBL-0132 | 24 | 2 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 2 | 001-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1188
10-LT-2132A | AI | CBL-0132 | 24 | 3 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 3 | 001-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):354
10-FT-2133A | AI | CBL-0132 | 24 | 4 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 4 | 001-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1401
10-TT-2134A | AI | CBL-0132 | 24 | 5 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 5 | 001-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1539
10-LT-2135A | AI | CBL-0132 | 24 | 6 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 6 | 001-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):700
10-LV-2136A | AO | CBL-0132 | 24 | 7 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 7 | 001-CBP-3-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):592
10-PT-2137A | AI | CBL-0132 | 24 | 8 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 8 | 001-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):904
10-PS-2138A | DI | CBL-0132 | 24 | 9 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 9 | 001-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):935
10-PS-2139A | DI | CBL-0132 | 24 | 10 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 10 | 001-CBP-3-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1035
10-LT-2140A | AI | CBL-0132 | 24 | 11 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 11 | 001-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1210
10-HS-2141A | DI | CBL-0132 | 24 | 12 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-3 | 12 | 001-CBP-3-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1923
10-TT-2142A | AI | CBL-0132 | 24 | 13 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 1 | 001-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):707
10-TT-2143A | AI | CBL-0132 | 24 | 14 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 2 | 001-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1885
10-FT-2144A | AI | CBL-0132 | 24 | 15 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 3 | 001-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):308
10-TT-2145A | AI | CBL-0132 | 24 | 16 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 4 | 001-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1043
10-LV-2146A | AO | CBL-0132 | 24 | 17 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 5 | 001-CBP-4-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1057
10-MY-2147A | DO-RELAY | CBL-0132 | 24 | 18 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 6 | 001-CBP-4-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):186
10-XV-2148A | DO-SOV | CBL-0132 | 24 | 19 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 7 | 001-CBP-4-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):681
10-LT-2149A | AI | CBL-0132 | 24 | 20 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 8 | 001-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1388
|  | CBL-0132 | 24 | 21 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 9 | 001-CBP-4-09 |  |  | Spare
|  | CBL-0132 | 24 | 22 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 10 | 001-CBP-4-10 |  |  | Spare
|  | CBL-0132 | 24 | 23 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 11 | 001-CBP-4-11 |  |  | Spare
|  | CBL-0132 | 24 | 24 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-4 | 12 | 001-CBP-4-12 |  |  | Spare
10-LT-1163A | AI | CBL-0017 | 12 | 1 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 1 | 001-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):875
10-PS-1164A | DI | CBL-0017 | 12 | 2 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 2 | 001-CBP-5-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):876
10-HN-1165A | DO-HORN | CBL-0017 | 12 | 3 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 3 | 001-CBP-5-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):204
10-TT-1166A | AI | CBL-0017 | 12 | 4 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 4 | 001-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1031
10-FV-1167A | AO | CBL-0017 | 12 | 5 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 5 | 001-CBP-5-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):62
10-LV-1168A | AO | CBL-0017 | 12 | 6 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 6 | 001-CBP-5-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1250
10-LS-1169A | DI | CBL-0017 | 12 | 7 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 7 | 001-CBP-5-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):24
10-TE-1170A | AI-RTD | CBL-0017 | 12 | 8 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 8 | 001-CBP-5-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):711
10-PT-1171A | AI | CBL-0017 | 12 | 9 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 9 | 001-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1925
|  | CBL-0017 | 12 | 10 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 10 | 001-CBP-5-10 |  |  | Spare
|  | CBL-0017 | 12 | 11 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 11 | 001-CBP-5-11 |  |  | Spare
|  | CBL-0017 | 12 | 12 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-5 | 12 | 001-CBP-5-12 |  |  | Spare
10-PT-1527A | AI | CBL-0062 | 12 | 1 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 1 | 001-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):209
10-HS-1528A | DI | CBL-0062 | 12 | 2 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 2 | 001-CBP-6-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):309
10-LV-1529A | AO | CBL-0062 | 12 | 3 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 3 | 001-CBP-6-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1831
10-FT-1530A | AI | CBL-0062 | 12 | 4 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 4 | 001-CBP-6-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1019
10-XY-1531A | DO | CBL-0062 | 12 | 5 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 5 | 001-CBP-6-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1672
10-MY-1532A | DO-RELAY | CBL-0062 | 12 | 6 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 6 | 001-CBP-6-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1565
10-PS-1533A | DI | CBL-0062 | 12 | 7 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 7 | 001-CBP-6-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):224
10-FT-1534A | AI | CBL-0062 | 12 | 8 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 8 | 001-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):189
10-TE-1535A | AI-RTD | CBL-0062 | 12 | 9 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 9 | 001-CBP-6-09 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1931
10-HY-1536A | DO | CBL-0062 | 12 | 10 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 10 | 001-CBP-6-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):185
|  | CBL-0062 | 12 | 11 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 11 | 001-CBP-6-11 |  |  | Spare
|  | CBL-0062 | 12 | 12 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-6 | 12 | 001-CBP-6-12 |  |  | Spare
10-ZS-1693A | DI | CBL-0085 | 12 | 1 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 1 | 001-CBP-7-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1421
10-PT-1694A | AI | CBL-0085 | 12 | 2 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 2 | 001-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1622
10-TE-1695A | AI-RTD | CBL-0085 | 12 | 3 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 3 | 001-CBP-7-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):478
10-PT-1696A | AI | CBL-0085 | 12 | 4 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 4 | 001-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):238
10-HS-1697A | DI | CBL-0085 | 12 | 5 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 5 | 001-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1233
10-PT-1698A | AI | CBL-0085 | 12 | 6 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 6 | 001-CBP-7-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):685
10-LT-1699A | AI | CBL-0085 | 12 | 7 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 7 | 001-CBP-7-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1794
10-PT-1700A | AI | CBL-0085 | 12 | 8 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 8 | 001-CBP-7-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):383
10-ZS-1701A | DI | CBL-0085 | 12 | 9 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 9 | 001-CBP-7-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):278
10-LS-1702A | DI | CBL-0085 | 12 | 10 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 10 | 001-CBP-7-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1502
10-LT-1703A | AI | CBL-0085 | 12 | 11 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 11 | 001-CBP-7-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):820
|  | CBL-0085 | 12 | 12 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-7 | 12 | 001-CBP-7-12 |  |  | Spare
10-LT-2227A | AI | CBL-0141 | 6 | 1 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 1 | 001-CBP-8-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):85
10-TT-2228A | AI | CBL-0141 | 6 | 2 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 2 | 001-CBP-8-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1348
10-TE-2229A | AI-RTD | CBL-0141 | 6 | 3 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 3 | 001-CBP-8-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):779
10-TT-2230A | AI | CBL-0141 | 6 | 4 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 4 | 001-CBP-8-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1846
10-XV-2231A | DO-SOV | CBL-0141 | 6 | 5 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 5 | 001-CBP-8-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):869
|  | CBL-0141 | 6 | 6 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 6 | 001-CBP-8-06 |  |  | Spare
10-LV-2366A | AO | CBL-0164 | 2 | 1 | G1 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 7 | 001-CBP-8-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):625
|  | CBL-0164 | 2 | 2 | G1 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 8 | 001-CBP-8-08 |  |  | Spare
10-TE-1182 | AI-RTD | CBL-0024 | 2 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 9 | 001-CBP-8-09 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1742
|  | CBL-0024 | 2 | 2 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 10 | 001-CBP-8-10 |  |  | Spare
10-ZS-1542 | DI | CBL-0067 | 2 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 11 | 001-CBP-8-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):781
|  | CBL-0067 | 2 | 2 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100001 | 001-CBP-8 | 12 | 001-CBP-8-12 |  |  | Spare
10-HY-1001 | DO | CBL-0001 | 24 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 1 | 002-CBP-1-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):406
10-FV-1002 | AO | CBL-0001 | 24 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 2 | 002-CBP-1-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):629
10-PT-1003 | AI | CBL-0001 | 24 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 3 | 002-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1092
10-XV-1004 | DO-SOV | CBL-0001 | 24 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 4 | 002-CBP-1-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):353
10-HS-1005 | DI | CBL-0001 | 24 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 5 | 002-CBP-1-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1440
10-LV-1006 | AO | CBL-0001 | 24 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 6 | 002-CBP-1-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1062
10-FV-1007 | AO | CBL-0001 | 24 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 7 | 002-CBP-1-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):814
10-HS-1008 | DI | CBL-0001 | 24 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 8 | 002-CBP-1-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1422
10-XV-1009 | DO-SOV | CBL-0001 | 24 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 9 | 002-CBP-1-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):254
10-PT-1010 | AI | CBL-0001 | 24 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 10 | 002-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1002
10-HN-1011 | DO-HORN | CBL-0001 | 24 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 11 | 002-CBP-1-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1006
10-LV-1012 | AO | CBL-0001 | 24 | 12 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-1 | 12 | 002-CBP-1-12 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):324
10-PV-1013 | AO | CBL-0001 | 24 | 13 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 1 | 002-CBP-2-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):706
10-TT-1014 | AI | CBL-0001 | 24 | 14 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 2 | 002-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1069
10-HN-1015 | DO-HORN | CBL-0001 | 24 | 15 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 3 | 002-CBP-2-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1331
10-FT-1016 | AI | CBL-0001 | 24 | 16 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 4 | 002-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1927
10-HY-1017 | DO | CBL-0001 | 24 | 17 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 5 | 002-CBP-2-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):580
10-HN-1018 | DO-HORN | CBL-0001 | 24 | 18 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 6 | 002-CBP-2-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):360
10-XV-1019 | DO-SOV | CBL-0001 | 24 | 19 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 7 | 002-CBP-2-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1366
10-LT-1020 | AI | CBL-0001 | 24 | 20 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 8 | 002-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):523
10-LT-1021 | AI | CBL-0001 | 24 | 21 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 9 | 002-CBP-2-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1817
10-XV-1022 | DO-SOV | CBL-0001 | 24 | 22 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 10 | 002-CBP-2-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1780
|  | CBL-0001 | 24 | 23 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 11 | 002-CBP-2-11 |  |  | Spare
|  | CBL-0001 | 24 | 24 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-2 | 12 | 002-CBP-2-12 |  |  | Spare
10-TT-1265 | AI | CBL-0035 | 24 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 1 | 002-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1607
10-TT-1266 | AI | CBL-0035 | 24 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 2 | 002-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1234
10-ZS-1267 | DI | CBL-0035 | 24 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 3 | 002-CBP-3-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):541
10-TE-1268 | AI-RTD | CBL-0035 | 24 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 4 | 002-CBP-3-04 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):378
10-HY-1269 | DO | CBL-0035 | 24 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 5 | 002-CBP-3-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1357
10-PS-1270 | DI | CBL-0035 | 24 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 6 | 002-CBP-3-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1518
10-LT-1271 | AI | CBL-0035 | 24 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 7 | 002-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1349
10-PT-1272 | AI | CBL-0035 | 24 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 8 | 002-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1047
10-XV-1273 | DO-SOV | CBL-0035 | 24 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 9 | 002-CBP-3-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1387
10-PT-1274 | AI | CBL-0035 | 24 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 10 | 002-CBP-3-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):993
10-XV-1275 | DO-SOV | CBL-0035 | 24 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 11 | 002-CBP-3-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):89
10-XV-1276 | DO-SOV | CBL-0035 | 24 | 12 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-3 | 12 | 002-CBP-3-12 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):929
10-XV-1277 | DO-SOV | CBL-0035 | 24 | 13 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 1 | 002-CBP-4-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):758
10-FT-1278 | AI | CBL-0035 | 24 | 14 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 2 | 002-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):184
10-XY-1279 | DO | CBL-0035 | 24 | 15 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 3 | 002-CBP-4-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1456
10-FT-1280 | AI | CBL-0035 | 24 | 16 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 4 | 002-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):446
10-XV-1281 | DO-SOV | CBL-0035 | 24 | 17 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 5 | 002-CBP-4-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1150
10-LS-1282 | DI | CBL-0035 | 24 | 18 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 6 | 002-CBP-4-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):940
10-TT-1283 | AI | CBL-0035 | 24 | 19 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 7 | 002-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1453
10-LV-1284 | AO | CBL-0035 | 24 | 20 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 8 | 002-CBP-4-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1983
|  | CBL-0035 | 24 | 21 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 9 | 002-CBP-4-09 |  |  | Spare
|  | CBL-0035 | 24 | 22 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 10 | 002-CBP-4-10 |  |  | Spare
|  | CBL-0035 | 24 | 23 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 11 | 002-CBP-4-11 |  |  | Spare
|  | CBL-0035 | 24 | 24 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-4 | 12 | 002-CBP-4-12 |  |  | Spare
10-FT-1286 | AI | CBL-0037 | 24 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 1 | 002-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):751
10-PV-1287 | AO | CBL-0037 | 24 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 2 | 002-CBP-5-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1494
10-XY-1288 | DO | CBL-0037 | 24 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 3 | 002-CBP-5-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):409
10-LV-1289 | AO | CBL-0037 | 24 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 4 | 002-CBP-5-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1572
10-LT-1290 | AI | CBL-0037 | 24 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 5 | 002-CBP-5-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):969
10-MY-1291 | DO-RELAY | CBL-0037 | 24 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 6 | 002-CBP-5-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1271
10-FT-1292 | AI | CBL-0037 | 24 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 7 | 002-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1576
10-PT-1293 | AI | CBL-0037 | 24 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 8 | 002-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):64
10-XV-1294 | DO-SOV | CBL-0037 | 24 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 9 | 002-CBP-5-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):2
10-PS-1295 | DI | CBL-0037 | 24 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 10 | 002-CBP-5-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):127
10-XV-1296 | DO-SOV | CBL-0037 | 24 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 11 | 002-CBP-5-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1775
10-PV-1297 | AO | CBL-0037 | 24 | 12 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-5 | 12 | 002-CBP-5-12 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1021
10-HS-1298 | DI | CBL-0037 | 24 | 13 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 1 | 002-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1343
10-PT-1299 | AI | CBL-0037 | 24 | 14 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 2 | 002-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):138
10-FT-1300 | AI | CBL-0037 | 24 | 15 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 3 | 002-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1471
10-XV-1301 | DO-SOV | CBL-0037 | 24 | 16 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 4 | 002-CBP-6-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1138
10-PT-1302 | AI | CBL-0037 | 24 | 17 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 5 | 002-CBP-6-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):111
10-XV-1303 | DO-SOV | CBL-0037 | 24 | 18 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 6 | 002-CBP-6-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1631
10-HS-1304 | DI | CBL-0037 | 24 | 19 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 7 | 002-CBP-6-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1361
10-TE-1305 | AI-RTD | CBL-0037 | 24 | 20 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 8 | 002-CBP-6-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1431
|  | CBL-0037 | 24 | 21 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 9 | 002-CBP-6-09 |  |  | Spare
|  | CBL-0037 | 24 | 22 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 10 | 002-CBP-6-10 |  |  | Spare
|  | CBL-0037 | 24 | 23 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 11 | 002-CBP-6-11 |  |  | Spare
|  | CBL-0037 | 24 | 24 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-6 | 12 | 002-CBP-6-12 |  |  | Spare
10-MY-1422 | DO-RELAY | CBL-0049 | 24 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 1 | 002-CBP-7-01 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):921
10-LT-1423 | AI | CBL-0049 | 24 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 2 | 002-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):829
10-FT-1424 | AI | CBL-0049 | 24 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 3 | 002-CBP-7-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1231
10-PS-1425 | DI | CBL-0049 | 24 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 4 | 002-CBP-7-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1801
10-FT-1426 | AI | CBL-0049 | 24 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 5 | 002-CBP-7-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1452
10-ZS-1427 | DI | CBL-0049 | 24 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 6 | 002-CBP-7-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):313
10-PV-1428 | AO | CBL-0049 | 24 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 7 | 002-CBP-7-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1989
10-PV-1429 | AO | CBL-0049 | 24 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 8 | 002-CBP-7-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):977
10-LT-1430 | AI | CBL-0049 | 24 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 9 | 002-CBP-7-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):319
10-ZS-1431 | DI | CBL-0049 | 24 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 10 | 002-CBP-7-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1535
10-FV-1432 | AO | CBL-0049 | 24 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 11 | 002-CBP-7-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):170
10-TT-1433 | AI | CBL-0049 | 24 | 12 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-7 | 12 | 002-CBP-7-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1958
10-HS-1434 | DI | CBL-0049 | 24 | 13 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 1 | 002-CBP-8-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1533
10-FT-1435 | AI | CBL-0049 | 24 | 14 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 2 | 002-CBP-8-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1940
10-FV-1436 | AO | CBL-0049 | 24 | 15 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 3 | 002-CBP-8-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):906
10-PT-1437 | AI | CBL-0049 | 24 | 16 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 4 | 002-CBP-8-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1423
10-HS-1438 | DI | CBL-0049 | 24 | 17 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 5 | 002-CBP-8-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1521
10-FT-1439 | AI | CBL-0049 | 24 | 18 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 6 | 002-CBP-8-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1501
10-LS-1440 | DI | CBL-0049 | 24 | 19 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 7 | 002-CBP-8-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):836
10-HS-1441 | DI | CBL-0049 | 24 | 20 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 8 | 002-CBP-8-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):687
|  | CBL-0049 | 24 | 21 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 9 | 002-CBP-8-09 |  |  | Spare
|  | CBL-0049 | 24 | 22 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 10 | 002-CBP-8-10 |  |  | Spare
|  | CBL-0049 | 24 | 23 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 11 | 002-CBP-8-11 |  |  | Spare
|  | CBL-0049 | 24 | 24 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100002 | 002-CBP-8 | 12 | 002-CBP-8-12 |  |  | Spare
10-FV-1446 | AO | CBL-0052 | 24 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 1 | 003-CBP-1-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1131
10-FT-1447 | AI | CBL-0052 | 24 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 2 | 003-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):547
10-PT-1448 | AI | CBL-0052 | 24 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 3 | 003-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1865
10-HS-1449 | DI | CBL-0052 | 24 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 4 | 003-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1323
10-TT-1450 | AI | CBL-0052 | 24 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 5 | 003-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):368
10-ZS-1451 | DI | CBL-0052 | 24 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 6 | 003-CBP-1-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):287
10-LT-1452 | AI | CBL-0052 | 24 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 7 | 003-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):393
10-LT-1453 | AI | CBL-0052 | 24 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 8 | 003-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):198
10-MY-1454 | DO-RELAY | CBL-0052 | 24 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 9 | 003-CBP-1-09 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):728
10-FT-1455 | AI | CBL-0052 | 24 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 10 | 003-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1610
10-LS-1456 | DI | CBL-0052 | 24 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 11 | 003-CBP-1-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1551
10-PS-1457 | DI | CBL-0052 | 24 | 12 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-1 | 12 | 003-CBP-1-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):108
10-PS-1458 | DI | CBL-0052 | 24 | 13 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 1 | 003-CBP-2-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1947
10-FT-1459 | AI | CBL-0052 | 24 | 14 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 2 | 003-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1004
10-PV-1460 | AO | CBL-0052 | 24 | 15 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 3 | 003-CBP-2-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1515
10-PT-1461 | AI | CBL-0052 | 24 | 16 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 4 | 003-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1754
10-FT-1462 | AI | CBL-0052 | 24 | 17 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 5 | 003-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):326
10-XV-1463 | DO-SOV | CBL-0052 | 24 | 18 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 6 | 003-CBP-2-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):274
10-LS-1464 | DI | CBL-0052 | 24 | 19 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 7 | 003-CBP-2-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1181
|  | CBL-0052 | 24 | 20 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 8 | 003-CBP-2-08 |  |  | Spare
|  | CBL-0052 | 24 | 21 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 9 | 003-CBP-2-09 |  |  | Spare
|  | CBL-0052 | 24 | 22 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 10 | 003-CBP-2-10 |  |  | Spare
|  | CBL-0052 | 24 | 23 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 11 | 003-CBP-2-11 |  |  | Spare
|  | CBL-0052 | 24 | 24 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-2 | 12 | 003-CBP-2-12 |  |  | Spare
10-PS-1498 | DI | CBL-0057 | 24 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 1 | 003-CBP-3-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):893
10-XV-1499 | DO-SOV | CBL-0057 | 24 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 2 | 003-CBP-3-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1648
10-TE-1500 | AI-RTD | CBL-0057 | 24 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 3 | 003-CBP-3-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):747
10-ZS-1501 | DI | CBL-0057 | 24 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 4 | 003-CBP-3-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):158
10-ZS-1502 | DI | CBL-0057 | 24 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 5 | 003-CBP-3-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1893
10-ZS-1503 | DI | CBL-0057 | 24 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 6 | 003-CBP-3-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):388
10-LT-1504 | AI | CBL-0057 | 24 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 7 | 003-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1301
10-TE-1505 | AI-RTD | CBL-0057 | 24 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 8 | 003-CBP-3-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):3
10-PV-1506 | AO | CBL-0057 | 24 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 9 | 003-CBP-3-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1472
10-PS-1507 | DI | CBL-0057 | 24 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 10 | 003-CBP-3-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1732
10-ZS-1508 | DI | CBL-0057 | 24 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 11 | 003-CBP-3-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):439
10-PS-1509 | DI | CBL-0057 | 24 | 12 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-3 | 12 | 003-CBP-3-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):684
10-PS-1510 | DI | CBL-0057 | 24 | 13 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 1 | 003-CBP-4-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):834
10-HN-1511 | DO-HORN | CBL-0057 | 24 | 14 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 2 | 003-CBP-4-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1906
10-TT-1512 | AI | CBL-0057 | 24 | 15 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 3 | 003-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):90
10-HS-1513 | DI | CBL-0057 | 24 | 16 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 4 | 003-CBP-4-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):789
10-FV-1514 | AO | CBL-0057 | 24 | 17 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 5 | 003-CBP-4-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):303
10-PS-1515 | DI | CBL-0057 | 24 | 18 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 6 | 003-CBP-4-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):657
10-LV-1516 | AO | CBL-0057 | 24 | 19 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 7 | 003-CBP-4-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1337
10-XV-1517 | DO-SOV | CBL-0057 | 24 | 20 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 8 | 003-CBP-4-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1611
|  | CBL-0057 | 24 | 21 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 9 | 003-CBP-4-09 |  |  | Spare
|  | CBL-0057 | 24 | 22 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 10 | 003-CBP-4-10 |  |  | Spare
|  | CBL-0057 | 24 | 23 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 11 | 003-CBP-4-11 |  |  | Spare
|  | CBL-0057 | 24 | 24 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-4 | 12 | 003-CBP-4-12 |  |  | Spare
10-XY-2527 | DO | CBL-0182 | 24 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 1 | 003-CBP-5-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1506
10-ZS-2528 | DI | CBL-0182 | 24 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 2 | 003-CBP-5-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):717
10-ZS-2529 | DI | CBL-0182 | 24 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 3 | 003-CBP-5-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):696
10-TT-2530 | AI | CBL-0182 | 24 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 4 | 003-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1620
10-PT-2531 | AI | CBL-0182 | 24 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 5 | 003-CBP-5-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1204
10-PS-2532 | DI | CBL-0182 | 24 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 6 | 003-CBP-5-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1248
10-LT-2533 | AI | CBL-0182 | 24 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 7 | 003-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1307
10-LT-2534 | AI | CBL-0182 | 24 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 8 | 003-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1100
10-PV-2535 | AO | CBL-0182 | 24 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 9 | 003-CBP-5-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1091
10-XV-2536 | DO-SOV | CBL-0182 | 24 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 10 | 003-CBP-5-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):534
10-HY-2537 | DO | CBL-0182 | 24 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 11 | 003-CBP-5-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):867
10-PT-2538 | AI | CBL-0182 | 24 | 12 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-5 | 12 | 003-CBP-5-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1217
10-HS-2539 | DI | CBL-0182 | 24 | 13 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 1 | 003-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1967
10-LV-2540 | AO | CBL-0182 | 24 | 14 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 2 | 003-CBP-6-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1762
10-PT-2541 | AI | CBL-0182 | 24 | 15 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 3 | 003-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):440
10-FV-2542 | AO | CBL-0182 | 24 | 16 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 4 | 003-CBP-6-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):271
10-HS-2543 | DI | CBL-0182 | 24 | 17 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 5 | 003-CBP-6-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):600
10-MY-2544 | DO-RELAY | CBL-0182 | 24 | 18 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 6 | 003-CBP-6-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):699
10-LT-2545 | AI | CBL-0182 | 24 | 19 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 7 | 003-CBP-6-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1326
|  | CBL-0182 | 24 | 20 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 8 | 003-CBP-6-08 |  |  | Spare
|  | CBL-0182 | 24 | 21 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 9 | 003-CBP-6-09 |  |  | Spare
|  | CBL-0182 | 24 | 22 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 10 | 003-CBP-6-10 |  |  | Spare
|  | CBL-0182 | 24 | 23 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 11 | 003-CBP-6-11 |  |  | Spare
|  | CBL-0182 | 24 | 24 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-6 | 12 | 003-CBP-6-12 |  |  | Spare
10-HY-2624 | DO | CBL-0190 | 24 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 1 | 003-CBP-7-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):197
10-PS-2625 | DI | CBL-0190 | 24 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 2 | 003-CBP-7-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1747
10-XY-2626 | DO | CBL-0190 | 24 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 3 | 003-CBP-7-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1583
10-LT-2627 | AI | CBL-0190 | 24 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 4 | 003-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):380
10-FT-2628 | AI | CBL-0190 | 24 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 5 | 003-CBP-7-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1497
10-FT-2629 | AI | CBL-0190 | 24 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 6 | 003-CBP-7-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):146
10-LV-2630 | AO | CBL-0190 | 24 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 7 | 003-CBP-7-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1509
10-XY-2631 | DO | CBL-0190 | 24 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 8 | 003-CBP-7-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1534
10-XV-2632 | DO-SOV | CBL-0190 | 24 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 9 | 003-CBP-7-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):373
10-PS-2633 | DI | CBL-0190 | 24 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 10 | 003-CBP-7-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):673
10-PS-2634 | DI | CBL-0190 | 24 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 11 | 003-CBP-7-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1302
10-PS-2635 | DI | CBL-0190 | 24 | 12 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-7 | 12 | 003-CBP-7-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):124
10-FT-2636 | AI | CBL-0190 | 24 | 13 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 1 | 003-CBP-8-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):770
10-LS-2637 | DI | CBL-0190 | 24 | 14 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 2 | 003-CBP-8-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):145
10-ZS-2638 | DI | CBL-0190 | 24 | 15 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 3 | 003-CBP-8-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):236
10-ZS-2639 | DI | CBL-0190 | 24 | 16 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 4 | 003-CBP-8-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1034
10-XV-2640 | DO-SOV | CBL-0190 | 24 | 17 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 5 | 003-CBP-8-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):331
10-PV-2641 | AO | CBL-0190 | 24 | 18 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 6 | 003-CBP-8-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1448
10-FT-2642 | AI | CBL-0190 | 24 | 19 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 7 | 003-CBP-8-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):912
10-LV-2643 | AO | CBL-0190 | 24 | 20 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 8 | 003-CBP-8-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):716
10-PS-2644 | DI | CBL-0190 | 24 | 21 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 9 | 003-CBP-8-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):283
10-HN-2645 | DO-HORN | CBL-0190 | 24 | 22 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 10 | 003-CBP-8-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1872
|  | CBL-0190 | 24 | 23 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 11 | 003-CBP-8-11 |  |  | Spare
|  | CBL-0190 | 24 | 24 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100003 | 003-CBP-8 | 12 | 003-CBP-8-12 |  |  | Spare
10-PT-1185 | AI | CBL-0027 | 12 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 1 | 004-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):318
10-MY-1186 | DO-RELAY | CBL-0027 | 12 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 2 | 004-CBP-1-02 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):463
10-HS-1187 | DI | CBL-0027 | 12 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 3 | 004-CBP-1-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1702
10-PV-1188 | AO | CBL-0027 | 12 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 4 | 004-CBP-1-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1595
10-LT-1189 | AI | CBL-0027 | 12 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 5 | 004-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):163
10-LT-1190 | AI | CBL-0027 | 12 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 6 | 004-CBP-1-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1528
10-FT-1191 | AI | CBL-0027 | 12 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 7 | 004-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):476
10-LT-1192 | AI | CBL-0027 | 12 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 8 | 004-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):957
10-XV-1193 | DO-SOV | CBL-0027 | 12 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 9 | 004-CBP-1-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):2002
10-XY-1194 | DO | CBL-0027 | 12 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 10 | 004-CBP-1-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):136
|  | CBL-0027 | 12 | 11 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 11 | 004-CBP-1-11 |  |  | Spare
|  | CBL-0027 | 12 | 12 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-1 | 12 | 004-CBP-1-12 |  |  | Spare
10-XV-1195 | DO-SOV | CBL-0028 | 12 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 1 | 004-CBP-2-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1045
10-PT-1196 | AI | CBL-0028 | 12 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 2 | 004-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1148
10-XV-1197 | DO-SOV | CBL-0028 | 12 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 3 | 004-CBP-2-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):757
10-PT-1198 | AI | CBL-0028 | 12 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 4 | 004-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1676
10-ZS-1199 | DI | CBL-0028 | 12 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 5 | 004-CBP-2-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):211
10-LT-1200 | AI | CBL-0028 | 12 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 6 | 004-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):879
10-LS-1201 | DI | CBL-0028 | 12 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 7 | 004-CBP-2-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1895
10-LS-1202 | DI | CBL-0028 | 12 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 8 | 004-CBP-2-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):948
10-HY-1203 | DO | CBL-0028 | 12 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 9 | 004-CBP-2-09 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1283
10-TT-1204 | AI | CBL-0028 | 12 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 10 | 004-CBP-2-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1308
10-LV-1205 | AO | CBL-0028 | 12 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 11 | 004-CBP-2-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1293
|  | CBL-0028 | 12 | 12 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-2 | 12 | 004-CBP-2-12 |  |  | Spare
10-LV-1228 | AO | CBL-0031 | 12 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 1 | 004-CBP-3-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):7
10-PT-1229 | AI | CBL-0031 | 12 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 2 | 004-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):431
10-FV-1230 | AO | CBL-0031 | 12 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 3 | 004-CBP-3-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1281
10-FT-1231 | AI | CBL-0031 | 12 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 4 | 004-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):664
10-LV-1232 | AO | CBL-0031 | 12 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 5 | 004-CBP-3-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1425
10-LV-1233 | AO | CBL-0031 | 12 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 6 | 004-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):154
10-ZS-1234 | DI | CBL-0031 | 12 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 7 | 004-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):597
10-ZS-1235 | DI | CBL-0031 | 12 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 8 | 004-CBP-3-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):371
10-XV-1236 | DO-SOV | CBL-0031 | 12 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 9 | 004-CBP-3-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1053
|  | CBL-0031 | 12 | 10 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 10 | 004-CBP-3-10 |  |  | Spare
|  | CBL-0031 | 12 | 11 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 11 | 004-CBP-3-11 |  |  | Spare
|  | CBL-0031 | 12 | 12 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-3 | 12 | 004-CBP-3-12 |  |  | Spare
10-PS-2241 | DI | CBL-0144 | 12 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 1 | 004-CBP-4-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1833
10-XY-2242 | DO | CBL-0144 | 12 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 2 | 004-CBP-4-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):475
10-LT-2243 | AI | CBL-0144 | 12 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 3 | 004-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1237
10-FT-2244 | AI | CBL-0144 | 12 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 4 | 004-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):423
10-FT-2245 | AI | CBL-0144 | 12 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 5 | 004-CBP-4-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):930
10-HS-2246 | DI | CBL-0144 | 12 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 6 | 004-CBP-4-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1799
10-TT-2247 | AI | CBL-0144 | 12 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 7 | 004-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):771
10-FT-2248 | AI | CBL-0144 | 12 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 8 | 004-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1718
10-LS-2249 | DI | CBL-0144 | 12 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 9 | 004-CBP-4-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1686
10-PS-2250 | DI | CBL-0144 | 12 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 10 | 004-CBP-4-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):422
10-PT-2251 | AI | CBL-0144 | 12 | 11 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 11 | 004-CBP-4-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1027
|  | CBL-0144 | 12 | 12 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-01 | AR1CIOC100004 | 004-CBP-4 | 12 | 004-CBP-4-12 |  |  | Spare
10-FT-2367 | AI | CBL-0166 | 12 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 1 | 005-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):448
10-FT-2368 | AI | CBL-0166 | 12 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 2 | 005-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1996
10-XV-2369 | DO-SOV | CBL-0166 | 12 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 3 | 005-CBP-1-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1793
10-ZS-2370 | DI | CBL-0166 | 12 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 4 | 005-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1444
10-PT-2371 | AI | CBL-0166 | 12 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 5 | 005-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):17
10-LV-2372 | AO | CBL-0166 | 12 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 6 | 005-CBP-1-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):310
10-ZS-2373 | DI | CBL-0166 | 12 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 7 | 005-CBP-1-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1335
10-PS-2374 | DI | CBL-0166 | 12 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 8 | 005-CBP-1-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1429
10-ZS-2375 | DI | CBL-0166 | 12 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 9 | 005-CBP-1-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):256
10-FT-2376 | AI | CBL-0166 | 12 | 10 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 10 | 005-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1952
|  | CBL-0166 | 12 | 11 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 11 | 005-CBP-1-11 |  |  | Spare
|  | CBL-0166 | 12 | 12 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-1 | 12 | 005-CBP-1-12 |  |  | Spare
10-HN-2411 | DO-HORN | CBL-0173 | 12 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 1 | 005-CBP-2-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):611
10-PS-2412 | DI | CBL-0173 | 12 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 2 | 005-CBP-2-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):970
10-PS-2413 | DI | CBL-0173 | 12 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 3 | 005-CBP-2-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):938
10-TT-2414 | AI | CBL-0173 | 12 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 4 | 005-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):178
10-ZS-2415 | DI | CBL-0173 | 12 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 5 | 005-CBP-2-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):821
10-HS-2416 | DI | CBL-0173 | 12 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 6 | 005-CBP-2-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):873
10-HS-2417 | DI | CBL-0173 | 12 | 7 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 7 | 005-CBP-2-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):614
10-MY-2418 | DO-RELAY | CBL-0173 | 12 | 8 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 8 | 005-CBP-2-08 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1688
10-LV-2419 | AO | CBL-0173 | 12 | 9 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 9 | 005-CBP-2-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1005
|  | CBL-0173 | 12 | 10 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 10 | 005-CBP-2-10 |  |  | Spare
|  | CBL-0173 | 12 | 11 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 11 | 005-CBP-2-11 |  |  | Spare
|  | CBL-0173 | 12 | 12 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-2 | 12 | 005-CBP-2-12 |  |  | Spare
10-XV-1369 | DO-SOV | CBL-0041 | 6 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 1 | 005-CBP-3-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):51
10-TE-1370 | AI-RTD | CBL-0041 | 6 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 2 | 005-CBP-3-02 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):694
10-PS-1371 | DI | CBL-0041 | 6 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 3 | 005-CBP-3-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1708
10-LS-1372 | DI | CBL-0041 | 6 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 4 | 005-CBP-3-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1109
10-ZS-1373 | DI | CBL-0041 | 6 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 5 | 005-CBP-3-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):494
10-ZS-1374 | DI | CBL-0041 | 6 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 6 | 005-CBP-3-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):59
10-HS-1741 | DI | CBL-0096 | 6 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 7 | 005-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1462
10-FV-1742 | AO | CBL-0096 | 6 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 8 | 005-CBP-3-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):504
10-PV-1743 | AO | CBL-0096 | 6 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 9 | 005-CBP-3-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):411
10-MY-1744 | DO-RELAY | CBL-0096 | 6 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 10 | 005-CBP-3-10 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1849
10-XV-1745 | DO-SOV | CBL-0096 | 6 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 11 | 005-CBP-3-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):908
|  | CBL-0096 | 6 | 6 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-3 | 12 | 005-CBP-3-12 |  |  | Spare
10-PT-2191 | AI | CBL-0138 | 6 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 1 | 005-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):472
10-LV-2192 | AO | CBL-0138 | 6 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 2 | 005-CBP-4-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):775
10-LV-2193 | AO | CBL-0138 | 6 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 3 | 005-CBP-4-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):662
10-PT-2194 | AI | CBL-0138 | 6 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 4 | 005-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):434
10-LV-2195 | AO | CBL-0138 | 6 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 5 | 005-CBP-4-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1578
|  | CBL-0138 | 6 | 6 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 6 | 005-CBP-4-06 |  |  | Spare
10-LT-2377 | AI | CBL-0167 | 6 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 7 | 005-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1579
10-FT-2378 | AI | CBL-0167 | 6 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 8 | 005-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1899
10-LT-2379 | AI | CBL-0167 | 6 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 9 | 005-CBP-4-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):659
10-FV-2380 | AO | CBL-0167 | 6 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 10 | 005-CBP-4-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):872
10-FT-2381 | AI | CBL-0167 | 6 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 11 | 005-CBP-4-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):329
10-LS-2382 | DI | CBL-0167 | 6 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-4 | 12 | 005-CBP-4-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):16
10-XV-2387 | DO-SOV | CBL-0169 | 6 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 1 | 005-CBP-5-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1483
10-HS-2388 | DI | CBL-0169 | 6 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 2 | 005-CBP-5-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1919
10-TE-2389 | AI-RTD | CBL-0169 | 6 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 3 | 005-CBP-5-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):828
10-TE-2390 | AI-RTD | CBL-0169 | 6 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 4 | 005-CBP-5-04 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):837
|  | CBL-0169 | 6 | 5 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 5 | 005-CBP-5-05 |  |  | Spare
|  | CBL-0169 | 6 | 6 | G1 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 6 | 005-CBP-5-06 |  |  | Spare
10-HS-2646 | DI | CBL-0191 | 6 | 1 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 7 | 005-CBP-5-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1580
10-PT-2647 | AI | CBL-0191 | 6 | 2 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 8 | 005-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):802
10-FV-2648 | AO | CBL-0191 | 6 | 3 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 9 | 005-CBP-5-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):314
10-XV-2649 | DO-SOV | CBL-0191 | 6 | 4 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 10 | 005-CBP-5-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1329
10-HS-2650 | DI | CBL-0191 | 6 | 5 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 11 | 005-CBP-5-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1715
10-TT-2651 | AI | CBL-0191 | 6 | 6 | G1 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-5 | 12 | 005-CBP-5-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1637
10-HS-1705B | DI | CBL-0089 | 24 | 1 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 1 | 005-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1554
10-XY-1706B | DO | CBL-0089 | 24 | 2 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 2 | 005-CBP-6-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1850
10-LT-1707B | AI | CBL-0089 | 24 | 3 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 3 | 005-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1573
10-XV-1708B | DO-SOV | CBL-0089 | 24 | 4 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 4 | 005-CBP-6-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):223
10-LT-1709B | AI | CBL-0089 | 24 | 5 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 5 | 005-CBP-6-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):347
10-XV-1710B | DO-SOV | CBL-0089 | 24 | 6 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 6 | 005-CBP-6-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1182
10-TT-1711B | AI | CBL-0089 | 24 | 7 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 7 | 005-CBP-6-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):731
10-PT-1712B | AI | CBL-0089 | 24 | 8 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 8 | 005-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1206
10-LV-1713B | AO | CBL-0089 | 24 | 9 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 9 | 005-CBP-6-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1577
10-PT-1714B | AI | CBL-0089 | 24 | 10 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 10 | 005-CBP-6-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):601
10-ZS-1715B | DI | CBL-0089 | 24 | 11 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 11 | 005-CBP-6-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):258
10-FV-1716B | AO | CBL-0089 | 24 | 12 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-6 | 12 | 005-CBP-6-12 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):183
10-PT-1717B | AI | CBL-0089 | 24 | 13 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 1 | 005-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):157
10-FV-1718B | AO | CBL-0089 | 24 | 14 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 2 | 005-CBP-7-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):466
10-FT-1719B | AI | CBL-0089 | 24 | 15 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 3 | 005-CBP-7-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1324
10-HN-1720B | DO-HORN | CBL-0089 | 24 | 16 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 4 | 005-CBP-7-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):884
10-ZS-1721B | DI | CBL-0089 | 24 | 17 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 5 | 005-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1268
10-PV-1722B | AO | CBL-0089 | 24 | 18 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 6 | 005-CBP-7-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1835
10-FT-1723B | AI | CBL-0089 | 24 | 19 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 7 | 005-CBP-7-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):596
10-LT-1724B | AI | CBL-0089 | 24 | 20 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 8 | 005-CBP-7-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1279
|  | CBL-0089 | 24 | 21 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 9 | 005-CBP-7-09 |  |  | Spare
|  | CBL-0089 | 24 | 22 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 10 | 005-CBP-7-10 |  |  | Spare
|  | CBL-0089 | 24 | 23 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 11 | 005-CBP-7-11 |  |  | Spare
|  | CBL-0089 | 24 | 24 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100005 | 005-CBP-7 | 12 | 005-CBP-7-12 |  |  | Spare
10-ZS-2130B | DI | CBL-0133 | 24 | 1 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 1 | 006-CBP-1-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):918
10-TT-2131B | AI | CBL-0133 | 24 | 2 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 2 | 006-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1504
10-LT-2132B | AI | CBL-0133 | 24 | 3 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 3 | 006-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):636
10-FT-2133B | AI | CBL-0133 | 24 | 4 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 4 | 006-CBP-1-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):144
10-TT-2134B | AI | CBL-0133 | 24 | 5 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 5 | 006-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1654
10-LT-2135B | AI | CBL-0133 | 24 | 6 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 6 | 006-CBP-1-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1911
10-LV-2136B | AO | CBL-0133 | 24 | 7 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 7 | 006-CBP-1-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):654
10-PT-2137B | AI | CBL-0133 | 24 | 8 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 8 | 006-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):45
10-PS-2138B | DI | CBL-0133 | 24 | 9 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 9 | 006-CBP-1-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1321
10-PS-2139B | DI | CBL-0133 | 24 | 10 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 10 | 006-CBP-1-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):998
10-LT-2140B | AI | CBL-0133 | 24 | 11 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 11 | 006-CBP-1-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):352
10-HS-2141B | DI | CBL-0133 | 24 | 12 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-1 | 12 | 006-CBP-1-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1945
10-TT-2142B | AI | CBL-0133 | 24 | 13 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 1 | 006-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1082
10-TT-2143B | AI | CBL-0133 | 24 | 14 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 2 | 006-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):427
10-FT-2144B | AI | CBL-0133 | 24 | 15 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 3 | 006-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1988
10-TT-2145B | AI | CBL-0133 | 24 | 16 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 4 | 006-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):482
10-LV-2146B | AO | CBL-0133 | 24 | 17 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 5 | 006-CBP-2-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1426
10-MY-2147B | DO-RELAY | CBL-0133 | 24 | 18 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 6 | 006-CBP-2-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1964
|  | CBL-0133 | 24 | 19 | G1 | B | Held (TQ) | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 7 | 006-CBP-2-07 |  |  | Reserved
10-LT-2149B | AI | CBL-0133 | 24 | 20 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 8 | 006-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):453
|  | CBL-0133 | 24 | 21 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 9 | 006-CBP-2-09 |  |  | Spare
|  | CBL-0133 | 24 | 22 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 10 | 006-CBP-2-10 |  |  | Spare
|  | CBL-0133 | 24 | 23 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 11 | 006-CBP-2-11 |  |  | Spare
|  | CBL-0133 | 24 | 24 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-2 | 12 | 006-CBP-2-12 |  |  | Spare
10-LT-1163B | AI | CBL-0018 | 12 | 1 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 1 | 006-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1424
10-PS-1164B | DI | CBL-0018 | 12 | 2 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 2 | 006-CBP-3-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):639
10-HN-1165B | DO-HORN | CBL-0018 | 12 | 3 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 3 | 006-CBP-3-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1785
10-TT-1166B | AI | CBL-0018 | 12 | 4 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 4 | 006-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):928
10-FV-1167B | AO | CBL-0018 | 12 | 5 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 5 | 006-CBP-3-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):418
10-LV-1168B | AO | CBL-0018 | 12 | 6 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 6 | 006-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):265
10-LS-1169B | DI | CBL-0018 | 12 | 7 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 7 | 006-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1517
10-TE-1170B | AI-RTD | CBL-0018 | 12 | 8 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 8 | 006-CBP-3-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):539
10-PT-1171B | AI | CBL-0018 | 12 | 9 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 9 | 006-CBP-3-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):842
|  | CBL-0018 | 12 | 10 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 10 | 006-CBP-3-10 |  |  | Spare
|  | CBL-0018 | 12 | 11 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 11 | 006-CBP-3-11 |  |  | Spare
|  | CBL-0018 | 12 | 12 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-3 | 12 | 006-CBP-3-12 |  |  | Spare
10-PT-1527B | AI | CBL-0063 | 12 | 1 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 1 | 006-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):612
10-HS-1528B | DI | CBL-0063 | 12 | 2 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 2 | 006-CBP-4-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1665
10-LV-1529B | AO | CBL-0063 | 12 | 3 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 3 | 006-CBP-4-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):81
10-FT-1530B | AI | CBL-0063 | 12 | 4 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 4 | 006-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1813
10-XY-1531B | DO | CBL-0063 | 12 | 5 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 5 | 006-CBP-4-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1951
10-MY-1532B | DO-RELAY | CBL-0063 | 12 | 6 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 6 | 006-CBP-4-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):56
10-PS-1533B | DI | CBL-0063 | 12 | 7 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 7 | 006-CBP-4-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):858
10-FT-1534B | AI | CBL-0063 | 12 | 8 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 8 | 006-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1816
10-TE-1535B | AI-RTD | CBL-0063 | 12 | 9 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 9 | 006-CBP-4-09 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):42
10-HY-1536B | DO | CBL-0063 | 12 | 10 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 10 | 006-CBP-4-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):672
|  | CBL-0063 | 12 | 11 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 11 | 006-CBP-4-11 |  |  | Spare
|  | CBL-0063 | 12 | 12 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-4 | 12 | 006-CBP-4-12 |  |  | Spare
10-ZS-1693B | DI | CBL-0086 | 12 | 1 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 1 | 006-CBP-5-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):667
10-PT-1694B | AI | CBL-0086 | 12 | 2 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 2 | 006-CBP-5-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1197
10-TE-1695B | AI-RTD | CBL-0086 | 12 | 3 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 3 | 006-CBP-5-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1503
10-PT-1696B | AI | CBL-0086 | 12 | 4 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 4 | 006-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):907
10-HS-1697B | DI | CBL-0086 | 12 | 5 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 5 | 006-CBP-5-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):604
10-PT-1698B | AI | CBL-0086 | 12 | 6 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 6 | 006-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):251
10-LT-1699B | AI | CBL-0086 | 12 | 7 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 7 | 006-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1409
10-PT-1700B | AI | CBL-0086 | 12 | 8 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 8 | 006-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):586
10-ZS-1701B | DI | CBL-0086 | 12 | 9 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 9 | 006-CBP-5-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):241
10-LS-1702B | DI | CBL-0086 | 12 | 10 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 10 | 006-CBP-5-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):883
10-LT-1703B | AI | CBL-0086 | 12 | 11 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 11 | 006-CBP-5-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1011
|  | CBL-0086 | 12 | 12 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-5 | 12 | 006-CBP-5-12 |  |  | Spare
10-LT-2227B | AI | CBL-0142 | 6 | 1 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-6 | 1 | 006-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1968
10-TT-2228B | AI | CBL-0142 | 6 | 2 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-6 | 2 | 006-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):392
10-TE-2229B | AI-RTD | CBL-0142 | 6 | 3 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-6 | 3 | 006-CBP-6-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1098
10-TT-2230B | AI | CBL-0142 | 6 | 4 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-6 | 4 | 006-CBP-6-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):194
10-XV-2231B | DO-SOV | CBL-0142 | 6 | 5 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-6 | 5 | 006-CBP-6-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1353
|  | CBL-0142 | 6 | 6 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-6 | 6 | 006-CBP-6-06 |  |  | Spare
10-LV-2366B | AO | CBL-0165 | 2 | 1 | G1 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-6 | 7 | 006-CBP-6-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):481
|  | CBL-0165 | 2 | 2 | G1 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-02 | AR1CIOC100006 | 006-CBP-6 | 8 | 006-CBP-6-08 |  |  | Spare
10-XY-1898A | DO | CBL-0111 | 24 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 1 | 007-CBP-1-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):579
10-XV-1899A | DO-SOV | CBL-0111 | 24 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 2 | 007-CBP-1-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1259
10-TT-1900A | AI | CBL-0111 | 24 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 3 | 007-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):277
10-FV-1901A | AO | CBL-0111 | 24 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 4 | 007-CBP-1-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1060
10-LS-1902A | DI | CBL-0111 | 24 | 5 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 5 | 007-CBP-1-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1750
10-HN-1903A | DO-HORN | CBL-0111 | 24 | 6 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 6 | 007-CBP-1-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):21
10-LS-1904A | DI | CBL-0111 | 24 | 7 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 7 | 007-CBP-1-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1143
10-MY-1905A | DO-RELAY | CBL-0111 | 24 | 8 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 8 | 007-CBP-1-08 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1663
10-FT-1906A | AI | CBL-0111 | 24 | 9 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 9 | 007-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1398
10-PT-1907A | AI | CBL-0111 | 24 | 10 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 10 | 007-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1711
10-TT-1908A | AI | CBL-0111 | 24 | 11 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 11 | 007-CBP-1-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1116
10-PS-1909A | DI | CBL-0111 | 24 | 12 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-1 | 12 | 007-CBP-1-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):500
10-HS-1910A | DI | CBL-0111 | 24 | 13 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 1 | 007-CBP-2-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):762
10-PT-1911A | AI | CBL-0111 | 24 | 14 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 2 | 007-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):990
10-LT-1912A | AI | CBL-0111 | 24 | 15 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 3 | 007-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):346
10-ZS-1913A | DI | CBL-0111 | 24 | 16 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 4 | 007-CBP-2-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):972
10-PV-1914A | AO | CBL-0111 | 24 | 17 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 5 | 007-CBP-2-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):428
10-PS-1915A | DI | CBL-0111 | 24 | 18 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 6 | 007-CBP-2-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1183
10-XY-1916A | DO | CBL-0111 | 24 | 19 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 7 | 007-CBP-2-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1008
|  | CBL-0111 | 24 | 20 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 8 | 007-CBP-2-08 |  |  | Spare
|  | CBL-0111 | 24 | 21 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 9 | 007-CBP-2-09 |  |  | Spare
|  | CBL-0111 | 24 | 22 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 10 | 007-CBP-2-10 |  |  | Spare
|  | CBL-0111 | 24 | 23 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 11 | 007-CBP-2-11 |  |  | Spare
|  | CBL-0111 | 24 | 24 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-2 | 12 | 007-CBP-2-12 |  |  | Spare
10-TT-1930A | AI | CBL-0115 | 24 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 1 | 007-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1216
10-XV-1931A | DO-SOV | CBL-0115 | 24 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 2 | 007-CBP-3-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1809
10-TT-1932A | AI | CBL-0115 | 24 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 3 | 007-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1511
10-PS-1933A | DI | CBL-0115 | 24 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 4 | 007-CBP-3-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1532
10-PS-1934A | DI | CBL-0115 | 24 | 5 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 5 | 007-CBP-3-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):322
10-PV-1935A | AO | CBL-0115 | 24 | 6 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 6 | 007-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):966
10-LS-1936A | DI | CBL-0115 | 24 | 7 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 7 | 007-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1065
10-XV-1937A | DO-SOV | CBL-0115 | 24 | 8 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 8 | 007-CBP-3-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1378
10-LS-1938A | DI | CBL-0115 | 24 | 9 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 9 | 007-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1218
10-XV-1939A | DO-SOV | CBL-0115 | 24 | 10 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 10 | 007-CBP-3-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):678
10-HY-1940A | DO | CBL-0115 | 24 | 11 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 11 | 007-CBP-3-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):981
10-HS-1941A | DI | CBL-0115 | 24 | 12 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-3 | 12 | 007-CBP-3-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):759
10-FT-1942A | AI | CBL-0115 | 24 | 13 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 1 | 007-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):122
10-LV-1943A | AO | CBL-0115 | 24 | 14 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 2 | 007-CBP-4-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):607
10-ZS-1944A | DI | CBL-0115 | 24 | 15 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 3 | 007-CBP-4-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1342
10-TT-1945A | AI | CBL-0115 | 24 | 16 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 4 | 007-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1229
10-HY-1946A | DO | CBL-0115 | 24 | 17 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 5 | 007-CBP-4-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):619
10-TE-1947A | AI-RTD | CBL-0115 | 24 | 18 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 6 | 007-CBP-4-06 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1569
10-ZS-1948A | DI | CBL-0115 | 24 | 19 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 7 | 007-CBP-4-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1726
|  | CBL-0115 | 24 | 20 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 8 | 007-CBP-4-08 |  |  | Spare
|  | CBL-0115 | 24 | 21 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 9 | 007-CBP-4-09 |  |  | Spare
|  | CBL-0115 | 24 | 22 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 10 | 007-CBP-4-10 |  |  | Spare
|  | CBL-0115 | 24 | 23 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 11 | 007-CBP-4-11 |  |  | Spare
|  | CBL-0115 | 24 | 24 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-4 | 12 | 007-CBP-4-12 |  |  | Spare
10-LT-2508A | AI | CBL-0180 | 24 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 1 | 007-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):88
10-PT-2509A | AI | CBL-0180 | 24 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 2 | 007-CBP-5-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1605
10-PT-2510A | AI | CBL-0180 | 24 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 3 | 007-CBP-5-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):188
10-HN-2511A | DO-HORN | CBL-0180 | 24 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 4 | 007-CBP-5-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1484
10-ZS-2512A | DI | CBL-0180 | 24 | 5 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 5 | 007-CBP-5-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1693
10-HN-2513A | DO-HORN | CBL-0180 | 24 | 6 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 6 | 007-CBP-5-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):502
10-TT-2514A | AI | CBL-0180 | 24 | 7 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 7 | 007-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1933
10-HY-2515A | DO | CBL-0180 | 24 | 8 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 8 | 007-CBP-5-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1493
10-PS-2516A | DI | CBL-0180 | 24 | 9 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 9 | 007-CBP-5-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1838
10-XV-2517A | DO-SOV | CBL-0180 | 24 | 10 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 10 | 007-CBP-5-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1548
10-FT-2518A | AI | CBL-0180 | 24 | 11 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 11 | 007-CBP-5-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):107
10-HS-2519A | DI | CBL-0180 | 24 | 12 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-5 | 12 | 007-CBP-5-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):669
10-LS-2520A | DI | CBL-0180 | 24 | 13 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 1 | 007-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1810
10-ZS-2521A | DI | CBL-0180 | 24 | 14 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 2 | 007-CBP-6-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1291
10-FT-2522A | AI | CBL-0180 | 24 | 15 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 3 | 007-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1520
|  | CBL-0180 | 24 | 16 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 4 | 007-CBP-6-04 |  |  | Spare
10-TT-2524A | AI | CBL-0180 | 24 | 17 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 5 | 007-CBP-6-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1647
10-ZS-2525A | DI | CBL-0180 | 24 | 18 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 6 | 007-CBP-6-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1184
10-XY-2526A | DO | CBL-0180 | 24 | 19 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 7 | 007-CBP-6-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):515
|  | CBL-0180 | 24 | 20 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 8 | 007-CBP-6-08 |  |  | Spare
|  | CBL-0180 | 24 | 21 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 9 | 007-CBP-6-09 |  |  | Spare
|  | CBL-0180 | 24 | 22 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 10 | 007-CBP-6-10 |  |  | Spare
|  | CBL-0180 | 24 | 23 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 11 | 007-CBP-6-11 |  |  | Spare
|  | CBL-0180 | 24 | 24 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-6 | 12 | 007-CBP-6-12 |  |  | Spare
10-TE-1034A | AI-RTD | CBL-0003 | 12 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 1 | 007-CBP-7-01 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1252
10-ZS-1035A | DI | CBL-0003 | 12 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 2 | 007-CBP-7-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):959
10-LS-1036A | DI | CBL-0003 | 12 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 3 | 007-CBP-7-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):807
10-MY-1037A | DO-RELAY | CBL-0003 | 12 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 4 | 007-CBP-7-04 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1570
10-LS-1038A | DI | CBL-0003 | 12 | 5 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 5 | 007-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):233
10-PV-1039A | AO | CBL-0003 | 12 | 6 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 6 | 007-CBP-7-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1208
10-MY-1040A | DO-RELAY | CBL-0003 | 12 | 7 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 7 | 007-CBP-7-07 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):450
10-ZS-1041A | DI | CBL-0003 | 12 | 8 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 8 | 007-CBP-7-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):499
10-ZS-1042A | DI | CBL-0003 | 12 | 9 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 9 | 007-CBP-7-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):886
|  | CBL-0003 | 12 | 10 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 10 | 007-CBP-7-10 |  |  | Spare
|  | CBL-0003 | 12 | 11 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 11 | 007-CBP-7-11 |  |  | Spare
|  | CBL-0003 | 12 | 12 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-7 | 12 | 007-CBP-7-12 |  |  | Spare
10-LV-1256A | AO | CBL-0033 | 12 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 1 | 007-CBP-8-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1036
10-FT-1257A | AI | CBL-0033 | 12 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 2 | 007-CBP-8-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):152
10-PS-1258A | DI | CBL-0033 | 12 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 3 | 007-CBP-8-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1078
10-HN-1259A | DO-HORN | CBL-0033 | 12 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 4 | 007-CBP-8-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):812
10-PT-1260A | AI | CBL-0033 | 12 | 5 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 5 | 007-CBP-8-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1689
10-XV-1261A | DO-SOV | CBL-0033 | 12 | 6 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 6 | 007-CBP-8-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):205
10-LV-1262A | AO | CBL-0033 | 12 | 7 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 7 | 007-CBP-8-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1064
10-PV-1263A | AO | CBL-0033 | 12 | 8 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 8 | 007-CBP-8-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1824
10-MY-1264A | DO-RELAY | CBL-0033 | 12 | 9 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 9 | 007-CBP-8-09 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1552
|  | CBL-0033 | 12 | 10 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 10 | 007-CBP-8-10 |  |  | Spare
|  | CBL-0033 | 12 | 11 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 11 | 007-CBP-8-11 |  |  | Spare
|  | CBL-0033 | 12 | 12 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100007 | 007-CBP-8 | 12 | 007-CBP-8-12 |  |  | Spare
10-PT-2402A | AI | CBL-0171 | 12 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 1 | 008-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1546
10-LV-2403A | AO | CBL-0171 | 12 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 2 | 008-CBP-1-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1519
10-LS-2404A | DI | CBL-0171 | 12 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 3 | 008-CBP-1-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):738
10-HS-2405A | DI | CBL-0171 | 12 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 4 | 008-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):275
10-HS-2406A | DI | CBL-0171 | 12 | 5 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 5 | 008-CBP-1-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):857
10-LT-2407A | AI | CBL-0171 | 12 | 6 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 6 | 008-CBP-1-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1316
10-LV-2408A | AO | CBL-0171 | 12 | 7 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 7 | 008-CBP-1-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):316
10-TT-2409A | AI | CBL-0171 | 12 | 8 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 8 | 008-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):516
10-FT-2410A | AI | CBL-0171 | 12 | 9 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 9 | 008-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1249
|  | CBL-0171 | 12 | 10 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 10 | 008-CBP-1-10 |  |  | Spare
|  | CBL-0171 | 12 | 11 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 11 | 008-CBP-1-11 |  |  | Spare
|  | CBL-0171 | 12 | 12 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-1 | 12 | 008-CBP-1-12 |  |  | Spare
10-LT-1442A | AI | CBL-0050 | 6 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 1 | 008-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1480
10-TT-1443A | AI | CBL-0050 | 6 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 2 | 008-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1072
10-LT-1444A | AI | CBL-0050 | 6 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 3 | 008-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1632
10-PT-1445A | AI | CBL-0050 | 6 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 4 | 008-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):6
|  | CBL-0050 | 6 | 5 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 5 | 008-CBP-2-05 |  |  | Spare
|  | CBL-0050 | 6 | 6 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 6 | 008-CBP-2-06 |  |  | Spare
10-XV-1863A | DO-SOV | CBL-0105 | 6 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 7 | 008-CBP-2-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):633
10-LT-1864A | AI | CBL-0105 | 6 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 8 | 008-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):967
10-XV-1865A | DO-SOV | CBL-0105 | 6 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 9 | 008-CBP-2-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):402
10-PT-1866A | AI | CBL-0105 | 6 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 10 | 008-CBP-2-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):474
|  | CBL-0105 | 6 | 5 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 11 | 008-CBP-2-11 |  |  | Spare
|  | CBL-0105 | 6 | 6 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-2 | 12 | 008-CBP-2-12 |  |  | Spare
10-LS-2261A | DI | CBL-0147 | 6 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 1 | 008-CBP-3-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):589
10-LT-2262A | AI | CBL-0147 | 6 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 2 | 008-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1475
10-ZS-2263A | DI | CBL-0147 | 6 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 3 | 008-CBP-3-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1157
10-LT-2264A | AI | CBL-0147 | 6 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 4 | 008-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):176
10-HN-2265A | DO-HORN | CBL-0147 | 6 | 5 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 5 | 008-CBP-3-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):413
|  | CBL-0147 | 6 | 6 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 6 | 008-CBP-3-06 |  |  | Spare
10-LS-2335A | DI | CBL-0159 | 6 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 7 | 008-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):30
10-XV-2336A | DO-SOV | CBL-0159 | 6 | 2 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 8 | 008-CBP-3-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):743
10-LT-2337A | AI | CBL-0159 | 6 | 3 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 9 | 008-CBP-3-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1333
10-XY-2338A | DO | CBL-0159 | 6 | 4 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 10 | 008-CBP-3-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):304
10-PV-2339A | AO | CBL-0159 | 6 | 5 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 11 | 008-CBP-3-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):512
|  | CBL-0159 | 6 | 6 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-3 | 12 | 008-CBP-3-12 |  |  | Spare
10-HY-1673A | DO | CBL-0082 | 2 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 1 | 008-CBP-4-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1667
|  | CBL-0082 | 2 | 2 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 2 | 008-CBP-4-02 |  |  | Spare
10-PT-1736A | AI | CBL-0093 | 2 | 1 | G2 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 3 | 008-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):384
|  | CBL-0093 | 2 | 2 | G2 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 4 | 008-CBP-4-04 |  |  | Spare
10-HS-1178 | DI | CBL-0023 | 6 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 5 | 008-CBP-4-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1169
10-XY-1179 | DO | CBL-0023 | 6 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 6 | 008-CBP-4-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1777
10-PT-1180 | AI | CBL-0023 | 6 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 7 | 008-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):956
10-MY-1181 | DO-RELAY | CBL-0023 | 6 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 8 | 008-CBP-4-08 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1368
|  | CBL-0023 | 6 | 5 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 9 | 008-CBP-4-09 |  |  | Spare
|  | CBL-0023 | 6 | 6 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 10 | 008-CBP-4-10 |  |  | Spare
10-LS-1083 | DI | CBL-0009 | 2 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 11 | 008-CBP-4-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):58
|  | CBL-0009 | 2 | 2 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-4 | 12 | 008-CBP-4-12 |  |  | Spare
10-FT-1561 | AI | CBL-0070 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 1 | 008-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1690
10-HY-1562 | DO | CBL-0070 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 2 | 008-CBP-5-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1395
10-PV-1563 | AO | CBL-0070 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 3 | 008-CBP-5-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):766
10-LT-1564 | AI | CBL-0070 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 4 | 008-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):248
10-PV-1565 | AO | CBL-0070 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 5 | 008-CBP-5-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):442
10-FT-1566 | AI | CBL-0070 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 6 | 008-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):878
10-TE-1567 | AI-RTD | CBL-0070 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 7 | 008-CBP-5-07 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):853
10-PV-1568 | AO | CBL-0070 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 8 | 008-CBP-5-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):32
10-LS-1569 | DI | CBL-0070 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 9 | 008-CBP-5-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1294
10-FT-1570 | AI | CBL-0070 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 10 | 008-CBP-5-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1716
10-PV-1571 | AO | CBL-0070 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 11 | 008-CBP-5-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1461
10-PS-1572 | DI | CBL-0070 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-5 | 12 | 008-CBP-5-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1977
10-MY-1573 | DO-RELAY | CBL-0070 | 24 | 13 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 1 | 008-CBP-6-01 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):335
10-PS-1574 | DI | CBL-0070 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 2 | 008-CBP-6-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1146
10-FT-1575 | AI | CBL-0070 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 3 | 008-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):464
10-PT-1576 | AI | CBL-0070 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 4 | 008-CBP-6-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):28
10-HS-1577 | DI | CBL-0070 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 5 | 008-CBP-6-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1192
10-PS-1578 | DI | CBL-0070 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 6 | 008-CBP-6-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):20
10-HY-1579 | DO | CBL-0070 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 7 | 008-CBP-6-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):574
10-XV-1580 | DO-SOV | CBL-0070 | 24 | 20 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 8 | 008-CBP-6-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1330
10-PT-1581 | AI | CBL-0070 | 24 | 21 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 9 | 008-CBP-6-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1405
10-XV-1582 | DO-SOV | CBL-0070 | 24 | 22 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 10 | 008-CBP-6-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):854
|  | CBL-0070 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 11 | 008-CBP-6-11 |  |  | Spare
|  | CBL-0070 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-6 | 12 | 008-CBP-6-12 |  |  | Spare
10-ZS-1583 | DI | CBL-0071 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 1 | 008-CBP-7-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):454
10-PT-1584 | AI | CBL-0071 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 2 | 008-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):147
10-PT-1585 | AI | CBL-0071 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 3 | 008-CBP-7-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1680
10-ZS-1586 | DI | CBL-0071 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 4 | 008-CBP-7-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):881
10-XV-1587 | DO-SOV | CBL-0071 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 5 | 008-CBP-7-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):514
10-HS-1588 | DI | CBL-0071 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 6 | 008-CBP-7-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1340
10-TE-1589 | AI-RTD | CBL-0071 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 7 | 008-CBP-7-07 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):911
10-TT-1590 | AI | CBL-0071 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 8 | 008-CBP-7-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1194
10-HY-1591 | DO | CBL-0071 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 9 | 008-CBP-7-09 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1699
10-LS-1592 | DI | CBL-0071 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 10 | 008-CBP-7-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):882
10-HS-1593 | DI | CBL-0071 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 11 | 008-CBP-7-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1776
10-PS-1594 | DI | CBL-0071 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-7 | 12 | 008-CBP-7-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1674
|  | CBL-0071 | 24 | 13 | G2 |  | Held (TQ) | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 1 | 008-CBP-8-01 |  |  | Reserved
10-LS-1596 | DI | CBL-0071 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 2 | 008-CBP-8-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):424
10-HY-1597 | DO | CBL-0071 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 3 | 008-CBP-8-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):429
10-LT-1598 | AI | CBL-0071 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 4 | 008-CBP-8-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1070
10-HS-1599 | DI | CBL-0071 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 5 | 008-CBP-8-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1887
10-HS-1600 | DI | CBL-0071 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 6 | 008-CBP-8-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1791
10-PT-1601 | AI | CBL-0071 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 7 | 008-CBP-8-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):269
10-LT-1602 | AI | CBL-0071 | 24 | 20 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 8 | 008-CBP-8-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):647
10-LT-1603 | AI | CBL-0071 | 24 | 21 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 9 | 008-CBP-8-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1200
10-XY-1604 | DO | CBL-0071 | 24 | 22 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 10 | 008-CBP-8-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):68
|  | CBL-0071 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 11 | 008-CBP-8-11 |  |  | Spare
|  | CBL-0071 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100008 | 008-CBP-8 | 12 | 008-CBP-8-12 |  |  | Spare
10-HS-1768 | DI | CBL-0098 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 1 | 009-CBP-1-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):447
10-TT-1769 | AI | CBL-0098 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 2 | 009-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1982
10-HS-1770 | DI | CBL-0098 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 3 | 009-CBP-1-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1441
10-XV-1771 | DO-SOV | CBL-0098 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 4 | 009-CBP-1-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):498
10-ZS-1772 | DI | CBL-0098 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 5 | 009-CBP-1-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1527
10-LS-1773 | DI | CBL-0098 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 6 | 009-CBP-1-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1007
10-PV-1774 | AO | CBL-0098 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 7 | 009-CBP-1-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):148
10-LV-1775 | AO | CBL-0098 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 8 | 009-CBP-1-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):763
10-HS-1776 | DI | CBL-0098 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 9 | 009-CBP-1-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):267
10-PS-1777 | DI | CBL-0098 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 10 | 009-CBP-1-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):564
10-XV-1778 | DO-SOV | CBL-0098 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 11 | 009-CBP-1-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1264
10-LT-1779 | AI | CBL-0098 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-1 | 12 | 009-CBP-1-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):670
10-FT-1780 | AI | CBL-0098 | 24 | 13 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 1 | 009-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):835
10-XV-1781 | DO-SOV | CBL-0098 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 2 | 009-CBP-2-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):257
10-LT-1782 | AI | CBL-0098 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 3 | 009-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):811
10-XV-1783 | DO-SOV | CBL-0098 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 4 | 009-CBP-2-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1890
10-HS-1784 | DI | CBL-0098 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 5 | 009-CBP-2-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1097
10-LT-1785 | AI | CBL-0098 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 6 | 009-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1240
10-TT-1786 | AI | CBL-0098 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 7 | 009-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):575
10-ZS-1787 | DI | CBL-0098 | 24 | 20 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 8 | 009-CBP-2-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1394
|  | CBL-0098 | 24 | 21 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 9 | 009-CBP-2-09 |  |  | Spare
|  | CBL-0098 | 24 | 22 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 10 | 009-CBP-2-10 |  |  | Spare
|  | CBL-0098 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 11 | 009-CBP-2-11 |  |  | Spare
|  | CBL-0098 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-2 | 12 | 009-CBP-2-12 |  |  | Spare
10-FV-2266 | AO | CBL-0149 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 1 | 009-CBP-3-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):819
10-LT-2267 | AI | CBL-0149 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 2 | 009-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):369
10-LV-2268 | AO | CBL-0149 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 3 | 009-CBP-3-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1656
10-XY-2269 | DO | CBL-0149 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 4 | 009-CBP-3-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1960
10-PT-2270 | AI | CBL-0149 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 5 | 009-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):399
10-HN-2271 | DO-HORN | CBL-0149 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 6 | 009-CBP-3-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1789
10-PS-2272 | DI | CBL-0149 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 7 | 009-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):350
10-LT-2273 | AI | CBL-0149 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 8 | 009-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):46
10-MY-2274 | DO-RELAY | CBL-0149 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 9 | 009-CBP-3-09 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):661
10-XY-2275 | DO | CBL-0149 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 10 | 009-CBP-3-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):668
10-HN-2276 | DO-HORN | CBL-0149 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 11 | 009-CBP-3-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1490
10-TT-2277 | AI | CBL-0149 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-3 | 12 | 009-CBP-3-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1864
10-XV-2278 | DO-SOV | CBL-0149 | 24 | 13 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 1 | 009-CBP-4-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1144
10-FV-2279 | AO | CBL-0149 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 2 | 009-CBP-4-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):173
10-HS-2280 | DI | CBL-0149 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 3 | 009-CBP-4-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1030
10-FT-2281 | AI | CBL-0149 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 4 | 009-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):841
10-HY-2282 | DO | CBL-0149 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 5 | 009-CBP-4-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1757
10-XV-2283 | DO-SOV | CBL-0149 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 6 | 009-CBP-4-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1863
10-HS-2284 | DI | CBL-0149 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 7 | 009-CBP-4-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):150
10-FT-2285 | AI | CBL-0149 | 24 | 20 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 8 | 009-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):874
10-FV-2286 | AO | CBL-0149 | 24 | 21 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 9 | 009-CBP-4-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1018
|  | CBL-0149 | 24 | 22 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 10 | 009-CBP-4-10 |  |  | Spare
|  | CBL-0149 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 11 | 009-CBP-4-11 |  |  | Spare
|  | CBL-0149 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-4 | 12 | 009-CBP-4-12 |  |  | Spare
10-LS-2340 | DI | CBL-0161 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 1 | 009-CBP-5-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1738
10-ZS-2341 | DI | CBL-0161 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 2 | 009-CBP-5-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1137
10-XY-2342 | DO | CBL-0161 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 3 | 009-CBP-5-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):133
10-HS-2343 | DI | CBL-0161 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 4 | 009-CBP-5-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):362
10-LT-2344 | AI | CBL-0161 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 5 | 009-CBP-5-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):129
10-LT-2345 | AI | CBL-0161 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 6 | 009-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1918
10-PT-2346 | AI | CBL-0161 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 7 | 009-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1306
10-PS-2347 | DI | CBL-0161 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 8 | 009-CBP-5-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):590
10-FT-2348 | AI | CBL-0161 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 9 | 009-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):951
10-LV-2349 | AO | CBL-0161 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 10 | 009-CBP-5-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1729
10-PT-2350 | AI | CBL-0161 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 11 | 009-CBP-5-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):865
10-XV-2351 | DO-SOV | CBL-0161 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-5 | 12 | 009-CBP-5-12 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):169
10-HN-2352 | DO-HORN | CBL-0161 | 24 | 13 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 1 | 009-CBP-6-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):94
10-MY-2353 | DO-RELAY | CBL-0161 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 2 | 009-CBP-6-02 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):395
10-LS-2354 | DI | CBL-0161 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 3 | 009-CBP-6-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):155
10-LS-2355 | DI | CBL-0161 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 4 | 009-CBP-6-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):909
10-XV-2356 | DO-SOV | CBL-0161 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 5 | 009-CBP-6-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):638
10-ZS-2357 | DI | CBL-0161 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 6 | 009-CBP-6-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1795
10-HY-2358 | DO | CBL-0161 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 7 | 009-CBP-6-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1413
10-PT-2359 | AI | CBL-0161 | 24 | 20 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 8 | 009-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1288
10-PT-2360 | AI | CBL-0161 | 24 | 21 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 9 | 009-CBP-6-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):221
|  | CBL-0161 | 24 | 22 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 10 | 009-CBP-6-10 |  |  | Spare
|  | CBL-0161 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 11 | 009-CBP-6-11 |  |  | Spare
|  | CBL-0161 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-6 | 12 | 009-CBP-6-12 |  |  | Spare
10-ZS-2420 | DI | CBL-0174 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 1 | 009-CBP-7-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):506
10-TT-2421 | AI | CBL-0174 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 2 | 009-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1915
10-PV-2422 | AO | CBL-0174 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 3 | 009-CBP-7-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1155
10-TT-2423 | AI | CBL-0174 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 4 | 009-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):899
10-XV-2424 | DO-SOV | CBL-0174 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 5 | 009-CBP-7-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):903
10-TT-2425 | AI | CBL-0174 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 6 | 009-CBP-7-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):642
10-TT-2426 | AI | CBL-0174 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 7 | 009-CBP-7-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):355
10-MY-2427 | DO-RELAY | CBL-0174 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 8 | 009-CBP-7-08 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):608
10-LT-2428 | AI | CBL-0174 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 9 | 009-CBP-7-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1847
10-LV-2429 | AO | CBL-0174 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 10 | 009-CBP-7-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):729
10-HN-2430 | DO-HORN | CBL-0174 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 11 | 009-CBP-7-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):370
10-XY-2431 | DO | CBL-0174 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-7 | 12 | 009-CBP-7-12 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1792
10-PT-2432 | AI | CBL-0174 | 24 | 13 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 1 | 009-CBP-8-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):546
10-HY-2433 | DO | CBL-0174 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 2 | 009-CBP-8-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1433
10-FT-2434 | AI | CBL-0174 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 3 | 009-CBP-8-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1032
10-HS-2435 | DI | CBL-0174 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 4 | 009-CBP-8-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1507
10-ZS-2436 | DI | CBL-0174 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 5 | 009-CBP-8-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):862
10-XY-2437 | DO | CBL-0174 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 6 | 009-CBP-8-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):656
10-XY-2438 | DO | CBL-0174 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 7 | 009-CBP-8-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1675
10-LT-2439 | AI | CBL-0174 | 24 | 20 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 8 | 009-CBP-8-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):495
|  | CBL-0174 | 24 | 21 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 9 | 009-CBP-8-09 |  |  | Spare
|  | CBL-0174 | 24 | 22 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 10 | 009-CBP-8-10 |  |  | Spare
|  | CBL-0174 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 11 | 009-CBP-8-11 |  |  | Spare
|  | CBL-0174 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100009 | 009-CBP-8 | 12 | 009-CBP-8-12 |  |  | Spare
10-PT-2546 | AI | CBL-0183 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 1 | 010-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1694
10-LT-2547 | AI | CBL-0183 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 2 | 010-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1295
10-PV-2548 | AO | CBL-0183 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 3 | 010-CBP-1-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):39
10-LS-2549 | DI | CBL-0183 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 4 | 010-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1588
10-HY-2550 | DO | CBL-0183 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 5 | 010-CBP-1-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1223
10-TE-2551 | AI-RTD | CBL-0183 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 6 | 010-CBP-1-06 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):139
10-PS-2552 | DI | CBL-0183 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 7 | 010-CBP-1-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1749
10-TT-2553 | AI | CBL-0183 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 8 | 010-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):249
10-LT-2554 | AI | CBL-0183 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 9 | 010-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1219
10-LS-2555 | DI | CBL-0183 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 10 | 010-CBP-1-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):898
10-XY-2556 | DO | CBL-0183 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 11 | 010-CBP-1-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):175
10-TT-2557 | AI | CBL-0183 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-1 | 12 | 010-CBP-1-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1272
10-PS-2558 | DI | CBL-0183 | 24 | 13 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 1 | 010-CBP-2-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1193
10-FT-2559 | AI | CBL-0183 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 2 | 010-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):128
10-TE-2560 | AI-RTD | CBL-0183 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 3 | 010-CBP-2-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):558
10-ZS-2561 | DI | CBL-0183 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 4 | 010-CBP-2-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1900
10-XY-2562 | DO | CBL-0183 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 5 | 010-CBP-2-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):182
10-FT-2563 | AI | CBL-0183 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 6 | 010-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1537
10-HY-2564 | DO | CBL-0183 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 7 | 010-CBP-2-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):27
10-LV-2565 | AO | CBL-0183 | 24 | 20 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 8 | 010-CBP-2-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1698
10-FT-2566 | AI | CBL-0183 | 24 | 21 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 9 | 010-CBP-2-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1371
10-TT-2567 | AI | CBL-0183 | 24 | 22 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 10 | 010-CBP-2-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):69
|  | CBL-0183 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 11 | 010-CBP-2-11 |  |  | Spare
|  | CBL-0183 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-2 | 12 | 010-CBP-2-12 |  |  | Spare
10-LV-2578 | AO | CBL-0185 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 1 | 010-CBP-3-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):544
10-PT-2579 | AI | CBL-0185 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 2 | 010-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1836
10-TT-2580 | AI | CBL-0185 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 3 | 010-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1556
10-PS-2581 | DI | CBL-0185 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 4 | 010-CBP-3-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):5
10-XY-2582 | DO | CBL-0185 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 5 | 010-CBP-3-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1235
10-TT-2583 | AI | CBL-0185 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 6 | 010-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):2001
10-LT-2584 | AI | CBL-0185 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 7 | 010-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1874
10-TE-2585 | AI-RTD | CBL-0185 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 8 | 010-CBP-3-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1866
10-LV-2586 | AO | CBL-0185 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 9 | 010-CBP-3-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):598
10-LV-2587 | AO | CBL-0185 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 10 | 010-CBP-3-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1703
10-PV-2588 | AO | CBL-0185 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 11 | 010-CBP-3-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1859
10-FT-2589 | AI | CBL-0185 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-3 | 12 | 010-CBP-3-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1084
10-FT-2590 | AI | CBL-0185 | 24 | 13 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 1 | 010-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):222
10-PS-2591 | DI | CBL-0185 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 2 | 010-CBP-4-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1289
10-PT-2592 | AI | CBL-0185 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 3 | 010-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1943
10-LT-2593 | AI | CBL-0185 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 4 | 010-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1876
10-LT-2594 | AI | CBL-0185 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 5 | 010-CBP-4-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):804
10-XY-2595 | DO | CBL-0185 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 6 | 010-CBP-4-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):18
10-FT-2596 | AI | CBL-0185 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 7 | 010-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1603
|  | CBL-0185 | 24 | 20 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 8 | 010-CBP-4-08 |  |  | Spare
|  | CBL-0185 | 24 | 21 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 9 | 010-CBP-4-09 |  |  | Spare
|  | CBL-0185 | 24 | 22 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 10 | 010-CBP-4-10 |  |  | Spare
|  | CBL-0185 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 11 | 010-CBP-4-11 |  |  | Spare
|  | CBL-0185 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-03 | AR1CIOC100010 | 010-CBP-4 | 12 | 010-CBP-4-12 |  |  | Spare
10-HS-2597 | DI | CBL-0186 | 24 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 1 | 011-CBP-1-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):125
10-XV-2598 | DO-SOV | CBL-0186 | 24 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 2 | 011-CBP-1-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):816
10-FT-2599 | AI | CBL-0186 | 24 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 3 | 011-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):143
10-LS-2600 | DI | CBL-0186 | 24 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 4 | 011-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1976
10-XV-2601 | DO-SOV | CBL-0186 | 24 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 5 | 011-CBP-1-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1196
10-PT-2602 | AI | CBL-0186 | 24 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 6 | 011-CBP-1-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):134
10-HY-2603 | DO | CBL-0186 | 24 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 7 | 011-CBP-1-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):671
10-PT-2604 | AI | CBL-0186 | 24 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 8 | 011-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1041
10-PS-2605 | DI | CBL-0186 | 24 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 9 | 011-CBP-1-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):923
10-XY-2606 | DO | CBL-0186 | 24 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 10 | 011-CBP-1-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):855
10-HY-2607 | DO | CBL-0186 | 24 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 11 | 011-CBP-1-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):311
10-PT-2608 | AI | CBL-0186 | 24 | 12 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-1 | 12 | 011-CBP-1-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1941
10-XY-2609 | DO | CBL-0186 | 24 | 13 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 1 | 011-CBP-2-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):177
10-ZS-2610 | DI | CBL-0186 | 24 | 14 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 2 | 011-CBP-2-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):159
10-PT-2611 | AI | CBL-0186 | 24 | 15 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 3 | 011-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1541
10-HY-2612 | DO | CBL-0186 | 24 | 16 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 4 | 011-CBP-2-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1039
10-XV-2613 | DO-SOV | CBL-0186 | 24 | 17 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 5 | 011-CBP-2-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1402
10-PT-2614 | AI | CBL-0186 | 24 | 18 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 6 | 011-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1797
10-TT-2615 | AI | CBL-0186 | 24 | 19 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 7 | 011-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):140
10-PT-2616 | AI | CBL-0186 | 24 | 20 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 8 | 011-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1380
10-LS-2617 | DI | CBL-0186 | 24 | 21 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 9 | 011-CBP-2-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1369
|  | CBL-0186 | 24 | 22 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 10 | 011-CBP-2-10 |  |  | Spare
|  | CBL-0186 | 24 | 23 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 11 | 011-CBP-2-11 |  |  | Spare
|  | CBL-0186 | 24 | 24 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-2 | 12 | 011-CBP-2-12 |  |  | Spare
10-TE-1023 | AI-RTD | CBL-0002 | 12 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 1 | 011-CBP-3-01 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):538
10-XV-1024 | DO-SOV | CBL-0002 | 12 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 2 | 011-CBP-3-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1212
10-HS-1025 | DI | CBL-0002 | 12 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 3 | 011-CBP-3-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1727
10-PS-1026 | DI | CBL-0002 | 12 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 4 | 011-CBP-3-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1924
10-ZS-1027 | DI | CBL-0002 | 12 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 5 | 011-CBP-3-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):866
10-LS-1028 | DI | CBL-0002 | 12 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 6 | 011-CBP-3-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):777
10-PT-1029 | AI | CBL-0002 | 12 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 7 | 011-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1280
10-HY-1030 | DO | CBL-0002 | 12 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 8 | 011-CBP-3-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1390
10-HS-1031 | DI | CBL-0002 | 12 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 9 | 011-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):420
10-LS-1032 | DI | CBL-0002 | 12 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 10 | 011-CBP-3-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1209
10-PV-1033 | AO | CBL-0002 | 12 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 11 | 011-CBP-3-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1147
|  | CBL-0002 | 12 | 12 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-3 | 12 | 011-CBP-3-12 |  |  | Spare
10-TE-1375 | AI-RTD | CBL-0042 | 12 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 1 | 011-CBP-4-01 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):888
10-PS-1376 | DI | CBL-0042 | 12 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 2 | 011-CBP-4-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1166
10-PT-1377 | AI | CBL-0042 | 12 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 3 | 011-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1786
10-XV-1378 | DO-SOV | CBL-0042 | 12 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 4 | 011-CBP-4-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1766
10-XV-1379 | DO-SOV | CBL-0042 | 12 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 5 | 011-CBP-4-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):818
10-LT-1380 | AI | CBL-0042 | 12 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 6 | 011-CBP-4-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):292
10-HY-1381 | DO | CBL-0042 | 12 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 7 | 011-CBP-4-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1591
10-LV-1382 | AO | CBL-0042 | 12 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 8 | 011-CBP-4-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1087
10-HY-1383 | DO | CBL-0042 | 12 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 9 | 011-CBP-4-09 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1948
|  | CBL-0042 | 12 | 10 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 10 | 011-CBP-4-10 |  |  | Spare
|  | CBL-0042 | 12 | 11 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 11 | 011-CBP-4-11 |  |  | Spare
|  | CBL-0042 | 12 | 12 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-4 | 12 | 011-CBP-4-12 |  |  | Spare
10-LT-1552 | AI | CBL-0069 | 12 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 1 | 011-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1904
10-LT-1553 | AI | CBL-0069 | 12 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 2 | 011-CBP-5-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):773
10-TT-1554 | AI | CBL-0069 | 12 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 3 | 011-CBP-5-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):568
10-PT-1555 | AI | CBL-0069 | 12 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 4 | 011-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1318
10-PS-1556 | DI | CBL-0069 | 12 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 5 | 011-CBP-5-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1597
10-PT-1557 | AI | CBL-0069 | 12 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 6 | 011-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):507
10-LT-1558 | AI | CBL-0069 | 12 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 7 | 011-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):167
10-FT-1559 | AI | CBL-0069 | 12 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 8 | 011-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):623
10-MY-1560 | DO-RELAY | CBL-0069 | 12 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 9 | 011-CBP-5-09 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1769
|  | CBL-0069 | 12 | 10 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 10 | 011-CBP-5-10 |  |  | Spare
|  | CBL-0069 | 12 | 11 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 11 | 011-CBP-5-11 |  |  | Spare
|  | CBL-0069 | 12 | 12 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-5 | 12 | 011-CBP-5-12 |  |  | Spare
10-XV-2064 | DO-SOV | CBL-0126 | 12 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 1 | 011-CBP-6-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1657
10-PT-2065 | AI | CBL-0126 | 12 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 2 | 011-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1722
10-FT-2066 | AI | CBL-0126 | 12 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 3 | 011-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1014
10-PT-2067 | AI | CBL-0126 | 12 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 4 | 011-CBP-6-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1042
10-LS-2068 | DI | CBL-0126 | 12 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 5 | 011-CBP-6-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):421
10-PT-2069 | AI | CBL-0126 | 12 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 6 | 011-CBP-6-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1666
10-LS-2070 | DI | CBL-0126 | 12 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 7 | 011-CBP-6-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1985
10-TT-2071 | AI | CBL-0126 | 12 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 8 | 011-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):65
10-XV-2072 | DO-SOV | CBL-0126 | 12 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 9 | 011-CBP-6-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):338
|  | CBL-0126 | 12 | 10 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 10 | 011-CBP-6-10 |  |  | Spare
|  | CBL-0126 | 12 | 11 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 11 | 011-CBP-6-11 |  |  | Spare
|  | CBL-0126 | 12 | 12 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-6 | 12 | 011-CBP-6-12 |  |  | Spare
10-TT-2150 | AI | CBL-0134 | 12 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 1 | 011-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1467
10-LT-2151 | AI | CBL-0134 | 12 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 2 | 011-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):391
10-ZS-2152 | DI | CBL-0134 | 12 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 3 | 011-CBP-7-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):161
10-XY-2153 | DO | CBL-0134 | 12 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 4 | 011-CBP-7-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1454
10-PT-2154 | AI | CBL-0134 | 12 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 5 | 011-CBP-7-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1526
10-ZS-2155 | DI | CBL-0134 | 12 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 6 | 011-CBP-7-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1819
10-TT-2156 | AI | CBL-0134 | 12 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 7 | 011-CBP-7-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):800
10-PS-2157 | DI | CBL-0134 | 12 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 8 | 011-CBP-7-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1336
10-XY-2158 | DO | CBL-0134 | 12 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 9 | 011-CBP-7-09 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1364
10-TT-2159 | AI | CBL-0134 | 12 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 10 | 011-CBP-7-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):101
10-XV-2160 | DO-SOV | CBL-0134 | 12 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 11 | 011-CBP-7-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1587
|  | CBL-0134 | 12 | 12 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-7 | 12 | 011-CBP-7-12 |  |  | Spare
10-FT-2171 | AI | CBL-0136 | 12 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 1 | 011-CBP-8-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):14
10-ZS-2172 | DI | CBL-0136 | 12 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 2 | 011-CBP-8-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1902
10-FT-2173 | AI | CBL-0136 | 12 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 3 | 011-CBP-8-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):210
10-HY-2174 | DO | CBL-0136 | 12 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 4 | 011-CBP-8-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):57
10-FT-2175 | AI | CBL-0136 | 12 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 5 | 011-CBP-8-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1386
10-LV-2176 | AO | CBL-0136 | 12 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 6 | 011-CBP-8-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1270
10-HS-2177 | DI | CBL-0136 | 12 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 7 | 011-CBP-8-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1126
10-HS-2178 | DI | CBL-0136 | 12 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 8 | 011-CBP-8-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1772
10-ZS-2179 | DI | CBL-0136 | 12 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 9 | 011-CBP-8-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1562
10-TT-2180 | AI | CBL-0136 | 12 | 10 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 10 | 011-CBP-8-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):479
10-LS-2181 | DI | CBL-0136 | 12 | 11 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 11 | 011-CBP-8-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):503
|  | CBL-0136 | 12 | 12 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100011 | 011-CBP-8 | 12 | 011-CBP-8-12 |  |  | Spare
10-HN-2232 | DO-HORN | CBL-0143 | 12 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 1 | 012-CBP-1-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1450
10-MY-2233 | DO-RELAY | CBL-0143 | 12 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 2 | 012-CBP-1-02 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):606
10-PT-2234 | AI | CBL-0143 | 12 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 3 | 012-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1017
10-PT-2235 | AI | CBL-0143 | 12 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 4 | 012-CBP-1-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):567
10-PV-2236 | AO | CBL-0143 | 12 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 5 | 012-CBP-1-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1370
10-LT-2237 | AI | CBL-0143 | 12 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 6 | 012-CBP-1-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1135
10-HS-2238 | DI | CBL-0143 | 12 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 7 | 012-CBP-1-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):377
10-XY-2239 | DO | CBL-0143 | 12 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 8 | 012-CBP-1-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1978
10-FT-2240 | AI | CBL-0143 | 12 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 9 | 012-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):263
|  | CBL-0143 | 12 | 10 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 10 | 012-CBP-1-10 |  |  | Spare
|  | CBL-0143 | 12 | 11 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 11 | 012-CBP-1-11 |  |  | Spare
|  | CBL-0143 | 12 | 12 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-1 | 12 | 012-CBP-1-12 |  |  | Spare
10-TT-2304 | AI | CBL-0155 | 12 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 1 | 012-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1074
10-LT-2305 | AI | CBL-0155 | 12 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 2 | 012-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):996
10-XY-2306 | DO | CBL-0155 | 12 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 3 | 012-CBP-2-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1840
10-XV-2307 | DO-SOV | CBL-0155 | 12 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 4 | 012-CBP-2-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):727
10-FT-2308 | AI | CBL-0155 | 12 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 5 | 012-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1375
10-TT-2309 | AI | CBL-0155 | 12 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 6 | 012-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1695
10-HS-2310 | DI | CBL-0155 | 12 | 7 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 7 | 012-CBP-2-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1303
10-PS-2311 | DI | CBL-0155 | 12 | 8 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 8 | 012-CBP-2-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1376
10-TE-2312 | AI-RTD | CBL-0155 | 12 | 9 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 9 | 012-CBP-2-09 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):645
|  | CBL-0155 | 12 | 10 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 10 | 012-CBP-2-10 |  |  | Spare
|  | CBL-0155 | 12 | 11 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 11 | 012-CBP-2-11 |  |  | Spare
|  | CBL-0155 | 12 | 12 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-2 | 12 | 012-CBP-2-12 |  |  | Spare
10-PS-2297 | DI | CBL-0152 | 6 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 1 | 012-CBP-3-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1227
10-LV-2298 | AO | CBL-0152 | 6 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 2 | 012-CBP-3-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1557
10-FT-2299 | AI | CBL-0152 | 6 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 3 | 012-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):825
10-TE-2300 | AI-RTD | CBL-0152 | 6 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 4 | 012-CBP-3-04 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1400
10-LT-2301 | AI | CBL-0152 | 6 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 5 | 012-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1822
10-PT-2302 | AI | CBL-0152 | 6 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 6 | 012-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):953
10-HY-1537 | DO | CBL-0064 | 2 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 7 | 012-CBP-3-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1949
10-HY-1538 | DO | CBL-0064 | 2 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 8 | 012-CBP-3-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):8
10-LV-1897 | AO | CBL-0110 | 2 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 9 | 012-CBP-3-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1936
|  | CBL-0110 | 2 | 2 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 10 | 012-CBP-3-10 |  |  | Spare
10-PS-1988 | DI | CBL-0119 | 2 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 11 | 012-CBP-3-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):179
|  | CBL-0119 | 2 | 2 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-3 | 12 | 012-CBP-3-12 |  |  | Spare
10-XV-2314 | DO-SOV | CBL-0157 | 2 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-4 | 1 | 012-CBP-4-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1247
10-FV-2315 | AO | CBL-0157 | 2 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-4 | 2 | 012-CBP-4-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):255
10-XY-1898B | DO | CBL-0112 | 24 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 1 | 012-CBP-5-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):132
10-XV-1899B | DO-SOV | CBL-0112 | 24 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 2 | 012-CBP-5-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1926
10-TT-1900B | AI | CBL-0112 | 24 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 3 | 012-CBP-5-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1013
10-FV-1901B | AO | CBL-0112 | 24 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 4 | 012-CBP-5-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):813
10-LS-1902B | DI | CBL-0112 | 24 | 5 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 5 | 012-CBP-5-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1437
10-HN-1903B | DO-HORN | CBL-0112 | 24 | 6 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 6 | 012-CBP-5-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1117
10-LS-1904B | DI | CBL-0112 | 24 | 7 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 7 | 012-CBP-5-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):780
10-MY-1905B | DO-RELAY | CBL-0112 | 24 | 8 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 8 | 012-CBP-5-08 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):808
10-FT-1906B | AI | CBL-0112 | 24 | 9 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 9 | 012-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1946
10-PT-1907B | AI | CBL-0112 | 24 | 10 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 10 | 012-CBP-5-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):2000
10-TT-1908B | AI | CBL-0112 | 24 | 11 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 11 | 012-CBP-5-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):513
10-PS-1909B | DI | CBL-0112 | 24 | 12 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-5 | 12 | 012-CBP-5-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1222
10-HS-1910B | DI | CBL-0112 | 24 | 13 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 1 | 012-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1868
10-PT-1911B | AI | CBL-0112 | 24 | 14 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 2 | 012-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):219
10-LT-1912B | AI | CBL-0112 | 24 | 15 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 3 | 012-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1416
10-ZS-1913B | DI | CBL-0112 | 24 | 16 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 4 | 012-CBP-6-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):896
10-PV-1914B | AO | CBL-0112 | 24 | 17 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 5 | 012-CBP-6-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):77
10-PS-1915B | DI | CBL-0112 | 24 | 18 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 6 | 012-CBP-6-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):861
10-XY-1916B | DO | CBL-0112 | 24 | 19 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 7 | 012-CBP-6-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):508
|  | CBL-0112 | 24 | 20 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 8 | 012-CBP-6-08 |  |  | Spare
|  | CBL-0112 | 24 | 21 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 9 | 012-CBP-6-09 |  |  | Spare
|  | CBL-0112 | 24 | 22 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 10 | 012-CBP-6-10 |  |  | Spare
|  | CBL-0112 | 24 | 23 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 11 | 012-CBP-6-11 |  |  | Spare
|  | CBL-0112 | 24 | 24 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-6 | 12 | 012-CBP-6-12 |  |  | Spare
10-TT-1930B | AI | CBL-0116 | 24 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 1 | 012-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1049
10-XV-1931B | DO-SOV | CBL-0116 | 24 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 2 | 012-CBP-7-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1566
10-TT-1932B | AI | CBL-0116 | 24 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 3 | 012-CBP-7-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1372
10-PS-1933B | DI | CBL-0116 | 24 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 4 | 012-CBP-7-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):115
10-PS-1934B | DI | CBL-0116 | 24 | 5 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 5 | 012-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1320
10-PV-1935B | AO | CBL-0116 | 24 | 6 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 6 | 012-CBP-7-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1058
10-LS-1936B | DI | CBL-0116 | 24 | 7 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 7 | 012-CBP-7-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):999
10-XV-1937B | DO-SOV | CBL-0116 | 24 | 8 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 8 | 012-CBP-7-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):932
10-LS-1938B | DI | CBL-0116 | 24 | 9 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 9 | 012-CBP-7-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):761
10-XV-1939B | DO-SOV | CBL-0116 | 24 | 10 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 10 | 012-CBP-7-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):87
10-HY-1940B | DO | CBL-0116 | 24 | 11 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 11 | 012-CBP-7-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1225
10-HS-1941B | DI | CBL-0116 | 24 | 12 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-7 | 12 | 012-CBP-7-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):986
10-FT-1942B | AI | CBL-0116 | 24 | 13 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 1 | 012-CBP-8-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1913
10-LV-1943B | AO | CBL-0116 | 24 | 14 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 2 | 012-CBP-8-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1606
10-ZS-1944B | DI | CBL-0116 | 24 | 15 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 3 | 012-CBP-8-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):296
10-TT-1945B | AI | CBL-0116 | 24 | 16 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 4 | 012-CBP-8-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):430
10-HY-1946B | DO | CBL-0116 | 24 | 17 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 5 | 012-CBP-8-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1458
10-TE-1947B | AI-RTD | CBL-0116 | 24 | 18 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 6 | 012-CBP-8-06 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1653
10-ZS-1948B | DI | CBL-0116 | 24 | 19 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 7 | 012-CBP-8-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1066
|  | CBL-0116 | 24 | 20 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 8 | 012-CBP-8-08 |  |  | Spare
|  | CBL-0116 | 24 | 21 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 9 | 012-CBP-8-09 |  |  | Spare
|  | CBL-0116 | 24 | 22 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 10 | 012-CBP-8-10 |  |  | Spare
|  | CBL-0116 | 24 | 23 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 11 | 012-CBP-8-11 |  |  | Spare
|  | CBL-0116 | 24 | 24 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100012 | 012-CBP-8 | 12 | 012-CBP-8-12 |  |  | Spare
10-LT-2508B | AI | CBL-0181 | 24 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 1 | 013-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):191
10-PT-2509B | AI | CBL-0181 | 24 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 2 | 013-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1828
10-PT-2510B | AI | CBL-0181 | 24 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 3 | 013-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1642
10-HN-2511B | DO-HORN | CBL-0181 | 24 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 4 | 013-CBP-1-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1602
10-ZS-2512B | DI | CBL-0181 | 24 | 5 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 5 | 013-CBP-1-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):616
10-HN-2513B | DO-HORN | CBL-0181 | 24 | 6 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 6 | 013-CBP-1-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):118
10-TT-2514B | AI | CBL-0181 | 24 | 7 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 7 | 013-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):266
10-HY-2515B | DO | CBL-0181 | 24 | 8 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 8 | 013-CBP-1-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1625
10-PS-2516B | DI | CBL-0181 | 24 | 9 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 9 | 013-CBP-1-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1633
10-XV-2517B | DO-SOV | CBL-0181 | 24 | 10 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 10 | 013-CBP-1-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):96
10-FT-2518B | AI | CBL-0181 | 24 | 11 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 11 | 013-CBP-1-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):246
10-HS-2519B | DI | CBL-0181 | 24 | 12 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-1 | 12 | 013-CBP-1-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1778
10-LS-2520B | DI | CBL-0181 | 24 | 13 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 1 | 013-CBP-2-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1884
10-ZS-2521B | DI | CBL-0181 | 24 | 14 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 2 | 013-CBP-2-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1531
10-FT-2522B | AI | CBL-0181 | 24 | 15 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 3 | 013-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):843
10-LT-2523B | AI | CBL-0181 | 24 | 16 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 4 | 013-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):396
10-TT-2524B | AI | CBL-0181 | 24 | 17 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 5 | 013-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):582
10-ZS-2525B | DI | CBL-0181 | 24 | 18 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 6 | 013-CBP-2-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1510
10-XY-2526B | DO | CBL-0181 | 24 | 19 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 7 | 013-CBP-2-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):214
|  | CBL-0181 | 24 | 20 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 8 | 013-CBP-2-08 |  |  | Spare
|  | CBL-0181 | 24 | 21 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 9 | 013-CBP-2-09 |  |  | Spare
|  | CBL-0181 | 24 | 22 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 10 | 013-CBP-2-10 |  |  | Spare
|  | CBL-0181 | 24 | 23 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 11 | 013-CBP-2-11 |  |  | Spare
|  | CBL-0181 | 24 | 24 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-2 | 12 | 013-CBP-2-12 |  |  | Spare
10-TE-1034B | AI-RTD | CBL-0004 | 12 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 1 | 013-CBP-3-01 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1474
10-ZS-1035B | DI | CBL-0004 | 12 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 2 | 013-CBP-3-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1609
10-LS-1036B | DI | CBL-0004 | 12 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 3 | 013-CBP-3-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1723
10-MY-1037B | DO-RELAY | CBL-0004 | 12 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 4 | 013-CBP-3-04 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):605
10-LS-1038B | DI | CBL-0004 | 12 | 5 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 5 | 013-CBP-3-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1263
10-PV-1039B | AO | CBL-0004 | 12 | 6 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 6 | 013-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):120
10-MY-1040B | DO-RELAY | CBL-0004 | 12 | 7 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 7 | 013-CBP-3-07 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):104
10-ZS-1041B | DI | CBL-0004 | 12 | 8 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 8 | 013-CBP-3-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):390
10-ZS-1042B | DI | CBL-0004 | 12 | 9 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 9 | 013-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):793
|  | CBL-0004 | 12 | 10 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 10 | 013-CBP-3-10 |  |  | Spare
|  | CBL-0004 | 12 | 11 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 11 | 013-CBP-3-11 |  |  | Spare
|  | CBL-0004 | 12 | 12 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-3 | 12 | 013-CBP-3-12 |  |  | Spare
10-LV-1256B | AO | CBL-0034 | 12 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 1 | 013-CBP-4-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):995
10-FT-1257B | AI | CBL-0034 | 12 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 2 | 013-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):437
10-PS-1258B | DI | CBL-0034 | 12 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 3 | 013-CBP-4-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):99
10-HN-1259B | DO-HORN | CBL-0034 | 12 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 4 | 013-CBP-4-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):628
10-PT-1260B | AI | CBL-0034 | 12 | 5 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 5 | 013-CBP-4-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1465
10-XV-1261B | DO-SOV | CBL-0034 | 12 | 6 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 6 | 013-CBP-4-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1419
10-LV-1262B | AO | CBL-0034 | 12 | 7 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 7 | 013-CBP-4-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):480
10-PV-1263B | AO | CBL-0034 | 12 | 8 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 8 | 013-CBP-4-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):415
10-MY-1264B | DO-RELAY | CBL-0034 | 12 | 9 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 9 | 013-CBP-4-09 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1561
|  | CBL-0034 | 12 | 10 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 10 | 013-CBP-4-10 |  |  | Spare
|  | CBL-0034 | 12 | 11 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 11 | 013-CBP-4-11 |  |  | Spare
|  | CBL-0034 | 12 | 12 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-4 | 12 | 013-CBP-4-12 |  |  | Spare
10-PT-2402B | AI | CBL-0172 | 12 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 1 | 013-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1037
10-LV-2403B | AO | CBL-0172 | 12 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 2 | 013-CBP-5-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):35
10-LS-2404B | DI | CBL-0172 | 12 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 3 | 013-CBP-5-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):870
10-HS-2405B | DI | CBL-0172 | 12 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 4 | 013-CBP-5-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):80
10-HS-2406B | DI | CBL-0172 | 12 | 5 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 5 | 013-CBP-5-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):721
10-LT-2407B | AI | CBL-0172 | 12 | 6 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 6 | 013-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1811
10-LV-2408B | AO | CBL-0172 | 12 | 7 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 7 | 013-CBP-5-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1829
10-TT-2409B | AI | CBL-0172 | 12 | 8 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 8 | 013-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):683
10-FT-2410B | AI | CBL-0172 | 12 | 9 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 9 | 013-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):910
|  | CBL-0172 | 12 | 10 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 10 | 013-CBP-5-10 |  |  | Spare
|  | CBL-0172 | 12 | 11 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 11 | 013-CBP-5-11 |  |  | Spare
|  | CBL-0172 | 12 | 12 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-5 | 12 | 013-CBP-5-12 |  |  | Spare
10-LT-1442B | AI | CBL-0051 | 6 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 1 | 013-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1646
10-TT-1443B | AI | CBL-0051 | 6 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 2 | 013-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):212
10-LT-1444B | AI | CBL-0051 | 6 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 3 | 013-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):610
10-PT-1445B | AI | CBL-0051 | 6 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 4 | 013-CBP-6-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):653
|  | CBL-0051 | 6 | 5 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 5 | 013-CBP-6-05 |  |  | Spare
|  | CBL-0051 | 6 | 6 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 6 | 013-CBP-6-06 |  |  | Spare
10-XV-1863B | DO-SOV | CBL-0106 | 6 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 7 | 013-CBP-6-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):280
10-LT-1864B | AI | CBL-0106 | 6 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 8 | 013-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1081
10-XV-1865B | DO-SOV | CBL-0106 | 6 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 9 | 013-CBP-6-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):624
10-PT-1866B | AI | CBL-0106 | 6 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 10 | 013-CBP-6-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):753
|  | CBL-0106 | 6 | 5 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 11 | 013-CBP-6-11 |  |  | Spare
|  | CBL-0106 | 6 | 6 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-6 | 12 | 013-CBP-6-12 |  |  | Spare
10-LS-2261B | DI | CBL-0148 | 6 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 1 | 013-CBP-7-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1093
10-LT-2262B | AI | CBL-0148 | 6 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 2 | 013-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1508
10-ZS-2263B | DI | CBL-0148 | 6 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 3 | 013-CBP-7-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):588
10-LT-2264B | AI | CBL-0148 | 6 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 4 | 013-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1275
10-HN-2265B | DO-HORN | CBL-0148 | 6 | 5 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 5 | 013-CBP-7-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):548
|  | CBL-0148 | 6 | 6 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 6 | 013-CBP-7-06 |  |  | Spare
10-LS-2335B | DI | CBL-0160 | 6 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 7 | 013-CBP-7-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1701
10-XV-2336B | DO-SOV | CBL-0160 | 6 | 2 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 8 | 013-CBP-7-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):227
10-LT-2337B | AI | CBL-0160 | 6 | 3 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 9 | 013-CBP-7-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):193
10-XY-2338B | DO | CBL-0160 | 6 | 4 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 10 | 013-CBP-7-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):71
10-PV-2339B | AO | CBL-0160 | 6 | 5 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 11 | 013-CBP-7-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):518
|  | CBL-0160 | 6 | 6 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-7 | 12 | 013-CBP-7-12 |  |  | Spare
10-HY-1673B | DO | CBL-0083 | 2 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 1 | 013-CBP-8-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):844
|  | CBL-0083 | 2 | 2 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 2 | 013-CBP-8-02 |  |  | Spare
10-PT-1736B | AI | CBL-0094 | 2 | 1 | G2 | B | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 3 | 013-CBP-8-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):195
|  | CBL-0094 | 2 | 2 | G2 | B | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 4 | 013-CBP-8-04 |  |  | Spare
10-PV-1475 | AO | CBL-0054 | 6 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 5 | 013-CBP-8-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):725
10-HS-1476 | DI | CBL-0054 | 6 | 2 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 6 | 013-CBP-8-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):114
10-HS-1477 | DI | CBL-0054 | 6 | 3 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 7 | 013-CBP-8-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):289
10-XV-1478 | DO-SOV | CBL-0054 | 6 | 4 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 8 | 013-CBP-8-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1974
10-HS-1479 | DI | CBL-0054 | 6 | 5 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 9 | 013-CBP-8-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):208
10-PS-1480 | DI | CBL-0054 | 6 | 6 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 10 | 013-CBP-8-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1878
10-LV-1520 | AO | CBL-0060 | 2 | 1 | G2 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 11 | 013-CBP-8-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1841
|  | CBL-0060 | 2 | 2 | G2 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-04 | AR1CIOC100013 | 013-CBP-8 | 12 | 013-CBP-8-12 |  |  | Spare
10-PT-1989A | AI | CBL-0120 | 24 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 1 | 014-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):785
10-LS-1990A | DI | CBL-0120 | 24 | 2 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 2 | 014-CBP-1-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1079
10-HY-1991A | DO | CBL-0120 | 24 | 3 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 3 | 014-CBP-1-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):130
10-TE-1992A | AI-RTD | CBL-0120 | 24 | 4 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 4 | 014-CBP-1-04 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1593
10-HY-1993A | DO | CBL-0120 | 24 | 5 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 5 | 014-CBP-1-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1022
10-LV-1994A | AO | CBL-0120 | 24 | 6 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 6 | 014-CBP-1-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1986
10-HS-1995A | DI | CBL-0120 | 24 | 7 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 7 | 014-CBP-1-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1277
10-TT-1996A | AI | CBL-0120 | 24 | 8 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 8 | 014-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):524
10-LV-1997A | AO | CBL-0120 | 24 | 9 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 9 | 014-CBP-1-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):279
10-LV-1998A | AO | CBL-0120 | 24 | 10 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 10 | 014-CBP-1-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):468
10-LT-1999A | AI | CBL-0120 | 24 | 11 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 11 | 014-CBP-1-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1389
10-FT-2000A | AI | CBL-0120 | 24 | 12 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-1 | 12 | 014-CBP-1-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):809
10-HS-2001A | DI | CBL-0120 | 24 | 13 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 1 | 014-CBP-2-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):980
10-LT-2002A | AI | CBL-0120 | 24 | 14 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 2 | 014-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):740
10-PV-2003A | AO | CBL-0120 | 24 | 15 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 3 | 014-CBP-2-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):634
10-PV-2004A | AO | CBL-0120 | 24 | 16 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 4 | 014-CBP-2-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1687
10-PS-2005A | DI | CBL-0120 | 24 | 17 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 5 | 014-CBP-2-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):100
10-XV-2006A | DO-SOV | CBL-0120 | 24 | 18 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 6 | 014-CBP-2-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1892
10-FV-2007A | AO | CBL-0120 | 24 | 19 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 7 | 014-CBP-2-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1187
10-HS-2008A | DI | CBL-0120 | 24 | 20 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 8 | 014-CBP-2-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1313
10-TT-2009A | AI | CBL-0120 | 24 | 21 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 9 | 014-CBP-2-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1842
10-FV-2010A | AO | CBL-0120 | 24 | 22 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 10 | 014-CBP-2-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):220
|  | CBL-0120 | 24 | 23 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 11 | 014-CBP-2-11 |  |  | Spare
|  | CBL-0120 | 24 | 24 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-2 | 12 | 014-CBP-2-12 |  |  | Spare
10-LS-2110A | DI | CBL-0130 | 24 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 1 | 014-CBP-3-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):200
10-PV-2111A | AO | CBL-0130 | 24 | 2 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 2 | 014-CBP-3-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1455
10-TT-2112A | AI | CBL-0130 | 24 | 3 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 3 | 014-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1152
10-LT-2113A | AI | CBL-0130 | 24 | 4 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 4 | 014-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):180
10-LT-2114A | AI | CBL-0130 | 24 | 5 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 5 | 014-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):527
10-PT-2115A | AI | CBL-0130 | 24 | 6 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 6 | 014-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1886
10-FT-2116A | AI | CBL-0130 | 24 | 7 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 7 | 014-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1764
10-PT-2117A | AI | CBL-0130 | 24 | 8 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 8 | 014-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):13
10-LT-2118A | AI | CBL-0130 | 24 | 9 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 9 | 014-CBP-3-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):718
10-PS-2119A | DI | CBL-0130 | 24 | 10 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 10 | 014-CBP-3-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1784
10-XV-2120A | DO-SOV | CBL-0130 | 24 | 11 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 11 | 014-CBP-3-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1678
10-FV-2121A | AO | CBL-0130 | 24 | 12 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-3 | 12 | 014-CBP-3-12 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):229
10-HS-2122A | DI | CBL-0130 | 24 | 13 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 1 | 014-CBP-4-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1246
10-HN-2123A | DO-HORN | CBL-0130 | 24 | 14 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 2 | 014-CBP-4-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):637
10-LT-2124A | AI | CBL-0130 | 24 | 15 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 3 | 014-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1741
10-LT-2125A | AI | CBL-0130 | 24 | 16 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 4 | 014-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):333
10-TT-2126A | AI | CBL-0130 | 24 | 17 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 5 | 014-CBP-4-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1867
10-LS-2127A | DI | CBL-0130 | 24 | 18 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 6 | 014-CBP-4-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):149
|  | CBL-0130 | 24 | 19 | G3 | A | Held (TQ) | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 7 | 014-CBP-4-07 |  |  | Reserved
10-FT-2129A | AI | CBL-0130 | 24 | 20 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 8 | 014-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1317
|  | CBL-0130 | 24 | 21 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 9 | 014-CBP-4-09 |  |  | Spare
|  | CBL-0130 | 24 | 22 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 10 | 014-CBP-4-10 |  |  | Spare
|  | CBL-0130 | 24 | 23 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 11 | 014-CBP-4-11 |  |  | Spare
|  | CBL-0130 | 24 | 24 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-4 | 12 | 014-CBP-4-12 |  |  | Spare
10-LT-2488A | AI | CBL-0178 | 24 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 1 | 014-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1879
10-TE-2489A | AI-RTD | CBL-0178 | 24 | 2 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 2 | 014-CBP-5-02 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1861
10-FT-2490A | AI | CBL-0178 | 24 | 3 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 3 | 014-CBP-5-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1243
10-TT-2491A | AI | CBL-0178 | 24 | 4 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 4 | 014-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1916
10-XY-2492A | DO | CBL-0178 | 24 | 5 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 5 | 014-CBP-5-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1901
10-LS-2493A | DI | CBL-0178 | 24 | 6 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 6 | 014-CBP-5-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):34
10-MY-2494A | DO-RELAY | CBL-0178 | 24 | 7 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 7 | 014-CBP-5-07 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1095
10-PT-2495A | AI | CBL-0178 | 24 | 8 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 8 | 014-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1592
10-FT-2496A | AI | CBL-0178 | 24 | 9 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 9 | 014-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):253
10-LV-2497A | AO | CBL-0178 | 24 | 10 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 10 | 014-CBP-5-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1802
10-PS-2498A | DI | CBL-0178 | 24 | 11 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 11 | 014-CBP-5-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):462
10-HS-2499A | DI | CBL-0178 | 24 | 12 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-5 | 12 | 014-CBP-5-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1096
10-LT-2500A | AI | CBL-0178 | 24 | 13 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 1 | 014-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):620
10-LT-2501A | AI | CBL-0178 | 24 | 14 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 2 | 014-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1639
10-PS-2502A | DI | CBL-0178 | 24 | 15 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 3 | 014-CBP-6-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):218
10-HS-2503A | DI | CBL-0178 | 24 | 16 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 4 | 014-CBP-6-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):750
10-TT-2504A | AI | CBL-0178 | 24 | 17 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 5 | 014-CBP-6-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):537
10-TT-2505A | AI | CBL-0178 | 24 | 18 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 6 | 014-CBP-6-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):975
10-PT-2506A | AI | CBL-0178 | 24 | 19 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 7 | 014-CBP-6-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):989
10-HS-2507A | DI | CBL-0178 | 24 | 20 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 8 | 014-CBP-6-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1896
|  | CBL-0178 | 24 | 21 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 9 | 014-CBP-6-09 |  |  | Spare
|  | CBL-0178 | 24 | 22 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 10 | 014-CBP-6-10 |  |  | Spare
|  | CBL-0178 | 24 | 23 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 11 | 014-CBP-6-11 |  |  | Spare
|  | CBL-0178 | 24 | 24 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-6 | 12 | 014-CBP-6-12 |  |  | Spare
10-TT-1638A | AI | CBL-0076 | 12 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 1 | 014-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1362
10-LT-1639A | AI | CBL-0076 | 12 | 2 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 2 | 014-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1712
10-XV-1640A | DO-SOV | CBL-0076 | 12 | 3 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 3 | 014-CBP-7-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1705
10-PT-1641A | AI | CBL-0076 | 12 | 4 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 4 | 014-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1174
10-ZS-1642A | DI | CBL-0076 | 12 | 5 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 5 | 014-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):860
10-FT-1643A | AI | CBL-0076 | 12 | 6 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 6 | 014-CBP-7-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1498
10-LT-1644A | AI | CBL-0076 | 12 | 7 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 7 | 014-CBP-7-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1241
10-LT-1645A | AI | CBL-0076 | 12 | 8 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 8 | 014-CBP-7-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):38
10-PT-1646A | AI | CBL-0076 | 12 | 9 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 9 | 014-CBP-7-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):961
10-FT-1647A | AI | CBL-0076 | 12 | 10 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 10 | 014-CBP-7-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1359
10-LT-1648A | AI | CBL-0076 | 12 | 11 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 11 | 014-CBP-7-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):113
|  | CBL-0076 | 12 | 12 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-7 | 12 | 014-CBP-7-12 |  |  | Spare
10-FT-2252A | AI | CBL-0145 | 12 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 1 | 014-CBP-8-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1969
10-LS-2253A | DI | CBL-0145 | 12 | 2 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 2 | 014-CBP-8-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1164
10-XV-2254A | DO-SOV | CBL-0145 | 12 | 3 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 3 | 014-CBP-8-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):583
10-XY-2255A | DO | CBL-0145 | 12 | 4 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 4 | 014-CBP-8-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1108
10-PS-2256A | DI | CBL-0145 | 12 | 5 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 5 | 014-CBP-8-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):649
10-LT-2257A | AI | CBL-0145 | 12 | 6 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 6 | 014-CBP-8-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1856
10-PT-2258A | AI | CBL-0145 | 12 | 7 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 7 | 014-CBP-8-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1125
10-ZS-2259A | DI | CBL-0145 | 12 | 8 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 8 | 014-CBP-8-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):561
10-TT-2260A | AI | CBL-0145 | 12 | 9 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 9 | 014-CBP-8-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):602
|  | CBL-0145 | 12 | 10 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 10 | 014-CBP-8-10 |  |  | Spare
|  | CBL-0145 | 12 | 11 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 11 | 014-CBP-8-11 |  |  | Spare
|  | CBL-0145 | 12 | 12 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100014 | 014-CBP-8 | 12 | 014-CBP-8-12 |  |  | Spare
10-LT-1172A | AI | CBL-0019 | 6 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 1 | 015-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1685
10-XV-1173A | DO-SOV | CBL-0019 | 6 | 2 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 2 | 015-CBP-1-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1044
10-TT-1174A | AI | CBL-0019 | 6 | 3 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 3 | 015-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):532
10-HS-1175A | DI | CBL-0019 | 6 | 4 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 4 | 015-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1955
|  | CBL-0019 | 6 | 5 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 5 | 015-CBP-1-05 |  |  | Spare
|  | CBL-0019 | 6 | 6 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 6 | 015-CBP-1-06 |  |  | Spare
10-XV-2361A | DO-SOV | CBL-0162 | 6 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 7 | 015-CBP-1-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1489
10-HY-2362A | DO | CBL-0162 | 6 | 2 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 8 | 015-CBP-1-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):417
10-LS-2363A | DI | CBL-0162 | 6 | 3 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 9 | 015-CBP-1-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):160
10-HN-2364A | DO-HORN | CBL-0162 | 6 | 4 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 10 | 015-CBP-1-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):554
10-HY-2365A | DO | CBL-0162 | 6 | 5 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 11 | 015-CBP-1-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1104
|  | CBL-0162 | 6 | 6 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-1 | 12 | 015-CBP-1-12 |  |  | Spare
10-XY-1518A | DO | CBL-0058 | 2 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 1 | 015-CBP-2-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):92
10-PS-1519A | DI | CBL-0058 | 2 | 2 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 2 | 015-CBP-2-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1076
10-FT-1735A | AI | CBL-0091 | 2 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 3 | 015-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1709
|  | CBL-0091 | 2 | 2 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 4 | 015-CBP-2-04 |  |  | Spare
10-LT-2303A | AI | CBL-0153 | 2 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 5 | 015-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1806
|  | CBL-0153 | 2 | 2 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 6 | 015-CBP-2-06 |  |  | Spare
10-PT-2623A | AI | CBL-0188 | 2 | 1 | G3 | A | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 7 | 015-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1733
|  | CBL-0188 | 2 | 2 | G3 | A | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 8 | 015-CBP-2-08 |  |  | Spare
10-LV-1539 | AO | CBL-0065 | 2 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 9 | 015-CBP-2-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):933
|  | CBL-0065 | 2 | 2 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 10 | 015-CBP-2-10 |  |  | Spare
10-HS-1540 | DI | CBL-0066 | 2 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 11 | 015-CBP-2-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):593
10-FT-1541 | AI | CBL-0066 | 2 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-2 | 12 | 015-CBP-2-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1626
10-LS-1122 | DI | CBL-0014 | 24 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 1 | 015-CBP-3-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1351
10-HS-1123 | DI | CBL-0014 | 24 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 2 | 015-CBP-3-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):799
10-XV-1124 | DO-SOV | CBL-0014 | 24 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 3 | 015-CBP-3-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1873
10-FT-1125 | AI | CBL-0014 | 24 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 4 | 015-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1636
10-HY-1126 | DO | CBL-0014 | 24 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 5 | 015-CBP-3-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1124
10-LV-1127 | AO | CBL-0014 | 24 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 6 | 015-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1848
10-FT-1128 | AI | CBL-0014 | 24 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 7 | 015-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1466
10-FT-1129 | AI | CBL-0014 | 24 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 8 | 015-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):660
10-LS-1130 | DI | CBL-0014 | 24 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 9 | 015-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1909
10-TT-1131 | AI | CBL-0014 | 24 | 10 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 10 | 015-CBP-3-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):962
10-LT-1132 | AI | CBL-0014 | 24 | 11 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 11 | 015-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1393
10-MY-1133 | DO-RELAY | CBL-0014 | 24 | 12 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-3 | 12 | 015-CBP-3-12 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):286
10-MY-1134 | DO-RELAY | CBL-0014 | 24 | 13 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 1 | 015-CBP-4-01 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):641
10-LT-1135 | AI | CBL-0014 | 24 | 14 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 2 | 015-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):571
10-HY-1136 | DO | CBL-0014 | 24 | 15 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 3 | 015-CBP-4-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):174
10-PT-1137 | AI | CBL-0014 | 24 | 16 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 4 | 015-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1435
10-HS-1138 | DI | CBL-0014 | 24 | 17 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 5 | 015-CBP-4-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):722
10-PT-1139 | AI | CBL-0014 | 24 | 18 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 6 | 015-CBP-4-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1151
10-HY-1140 | DO | CBL-0014 | 24 | 19 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 7 | 015-CBP-4-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):387
10-PT-1141 | AI | CBL-0014 | 24 | 20 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 8 | 015-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1700
10-FV-1142 | AO | CBL-0014 | 24 | 21 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 9 | 015-CBP-4-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):341
|  | CBL-0014 | 24 | 22 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 10 | 015-CBP-4-10 |  |  | Spare
|  | CBL-0014 | 24 | 23 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 11 | 015-CBP-4-11 |  |  | Spare
|  | CBL-0014 | 24 | 24 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-4 | 12 | 015-CBP-4-12 |  |  | Spare
10-LT-1237 | AI | CBL-0032 | 24 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 1 | 015-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):153
10-FT-1238 | AI | CBL-0032 | 24 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 2 | 015-CBP-5-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):375
10-PS-1239 | DI | CBL-0032 | 24 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 3 | 015-CBP-5-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):493
10-LT-1240 | AI | CBL-0032 | 24 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 4 | 015-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):74
10-XV-1241 | DO-SOV | CBL-0032 | 24 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 5 | 015-CBP-5-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):432
10-LV-1242 | AO | CBL-0032 | 24 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 6 | 015-CBP-5-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):356
10-MY-1243 | DO-RELAY | CBL-0032 | 24 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 7 | 015-CBP-5-07 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1088
10-XV-1244 | DO-SOV | CBL-0032 | 24 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 8 | 015-CBP-5-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):713
10-XV-1245 | DO-SOV | CBL-0032 | 24 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 9 | 015-CBP-5-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):247
10-TT-1246 | AI | CBL-0032 | 24 | 10 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 10 | 015-CBP-5-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):833
10-HN-1247 | DO-HORN | CBL-0032 | 24 | 11 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 11 | 015-CBP-5-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):735
10-XY-1248 | DO | CBL-0032 | 24 | 12 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-5 | 12 | 015-CBP-5-12 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1473
10-FT-1249 | AI | CBL-0032 | 24 | 13 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 1 | 015-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1907
10-XV-1250 | DO-SOV | CBL-0032 | 24 | 14 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 2 | 015-CBP-6-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):676
10-ZS-1251 | DI | CBL-0032 | 24 | 15 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 3 | 015-CBP-6-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):859
10-LS-1252 | DI | CBL-0032 | 24 | 16 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 4 | 015-CBP-6-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1956
10-ZS-1253 | DI | CBL-0032 | 24 | 17 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 5 | 015-CBP-6-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1807
10-FT-1254 | AI | CBL-0032 | 24 | 18 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 6 | 015-CBP-6-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):936
10-XV-1255 | DO-SOV | CBL-0032 | 24 | 19 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 7 | 015-CBP-6-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1962
|  | CBL-0032 | 24 | 20 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 8 | 015-CBP-6-08 |  |  | Spare
|  | CBL-0032 | 24 | 21 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 9 | 015-CBP-6-09 |  |  | Spare
|  | CBL-0032 | 24 | 22 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 10 | 015-CBP-6-10 |  |  | Spare
|  | CBL-0032 | 24 | 23 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 11 | 015-CBP-6-11 |  |  | Spare
|  | CBL-0032 | 24 | 24 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-6 | 12 | 015-CBP-6-12 |  |  | Spare
10-PS-1841 | DI | CBL-0103 | 24 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 1 | 015-CBP-7-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):510
10-XV-1842 | DO-SOV | CBL-0103 | 24 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 2 | 015-CBP-7-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):490
10-LS-1843 | DI | CBL-0103 | 24 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 3 | 015-CBP-7-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1399
10-FT-1844 | AI | CBL-0103 | 24 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 4 | 015-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1404
10-ZS-1845 | DI | CBL-0103 | 24 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 5 | 015-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):401
10-XY-1846 | DO | CBL-0103 | 24 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 6 | 015-CBP-7-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):291
10-XV-1847 | DO-SOV | CBL-0103 | 24 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 7 | 015-CBP-7-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):894
10-PT-1848 | AI | CBL-0103 | 24 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 8 | 015-CBP-7-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):61
10-PS-1849 | DI | CBL-0103 | 24 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 9 | 015-CBP-7-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):627
10-LT-1850 | AI | CBL-0103 | 24 | 10 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 10 | 015-CBP-7-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):151
10-LS-1851 | DI | CBL-0103 | 24 | 11 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 11 | 015-CBP-7-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):919
10-PS-1852 | DI | CBL-0103 | 24 | 12 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-7 | 12 | 015-CBP-7-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):550
10-PS-1853 | DI | CBL-0103 | 24 | 13 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 1 | 015-CBP-8-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1513
10-LT-1854 | AI | CBL-0103 | 24 | 14 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 2 | 015-CBP-8-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1914
10-LV-1855 | AO | CBL-0103 | 24 | 15 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 3 | 015-CBP-8-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):791
10-LT-1856 | AI | CBL-0103 | 24 | 16 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 4 | 015-CBP-8-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1971
10-TT-1857 | AI | CBL-0103 | 24 | 17 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 5 | 015-CBP-8-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1725
10-FT-1858 | AI | CBL-0103 | 24 | 18 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 6 | 015-CBP-8-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1046
10-HS-1859 | DI | CBL-0103 | 24 | 19 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 7 | 015-CBP-8-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):285
10-LS-1860 | DI | CBL-0103 | 24 | 20 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 8 | 015-CBP-8-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):135
|  | CBL-0103 | 24 | 21 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 9 | 015-CBP-8-09 |  |  | Spare
|  | CBL-0103 | 24 | 22 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 10 | 015-CBP-8-10 |  |  | Spare
|  | CBL-0103 | 24 | 23 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 11 | 015-CBP-8-11 |  |  | Spare
|  | CBL-0103 | 24 | 24 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100015 | 015-CBP-8 | 12 | 015-CBP-8-12 |  |  | Spare
10-PT-2024 | AI | CBL-0124 | 24 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 1 | 016-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1677
10-LS-2025 | DI | CBL-0124 | 24 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 2 | 016-CBP-1-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1803
10-TT-2026 | AI | CBL-0124 | 24 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 3 | 016-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):806
10-LV-2027 | AO | CBL-0124 | 24 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 4 | 016-CBP-1-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):119
10-XV-2028 | DO-SOV | CBL-0124 | 24 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 5 | 016-CBP-1-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1768
10-XV-2029 | DO-SOV | CBL-0124 | 24 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 6 | 016-CBP-1-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):925
10-XV-2030 | DO-SOV | CBL-0124 | 24 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 7 | 016-CBP-1-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):964
10-FT-2031 | AI | CBL-0124 | 24 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 8 | 016-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1524
10-TE-2032 | AI-RTD | CBL-0124 | 24 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 9 | 016-CBP-1-09 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):927
10-LT-2033 | AI | CBL-0124 | 24 | 10 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 10 | 016-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):230
10-XV-2034 | DO-SOV | CBL-0124 | 24 | 11 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 11 | 016-CBP-1-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):530
10-PV-2035 | AO | CBL-0124 | 24 | 12 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-1 | 12 | 016-CBP-1-12 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):29
10-TT-2036 | AI | CBL-0124 | 24 | 13 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 1 | 016-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):234
10-FT-2037 | AI | CBL-0124 | 24 | 14 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 2 | 016-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):521
10-FT-2038 | AI | CBL-0124 | 24 | 15 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 3 | 016-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):216
10-XV-2039 | DO-SOV | CBL-0124 | 24 | 16 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 4 | 016-CBP-2-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):572
10-FT-2040 | AI | CBL-0124 | 24 | 17 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 5 | 016-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):752
10-PT-2041 | AI | CBL-0124 | 24 | 18 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 6 | 016-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1020
10-FT-2042 | AI | CBL-0124 | 24 | 19 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 7 | 016-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):491
|  | CBL-0124 | 24 | 20 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 8 | 016-CBP-2-08 |  |  | Spare
|  | CBL-0124 | 24 | 21 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 9 | 016-CBP-2-09 |  |  | Spare
|  | CBL-0124 | 24 | 22 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 10 | 016-CBP-2-10 |  |  | Spare
|  | CBL-0124 | 24 | 23 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 11 | 016-CBP-2-11 |  |  | Spare
|  | CBL-0124 | 24 | 24 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-2 | 12 | 016-CBP-2-12 |  |  | Spare
10-LT-1143 | AI | CBL-0015 | 12 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 1 | 016-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1492
10-FT-1144 | AI | CBL-0015 | 12 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 2 | 016-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):33
10-FT-1145 | AI | CBL-0015 | 12 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 3 | 016-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1818
10-TE-1146 | AI-RTD | CBL-0015 | 12 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 4 | 016-CBP-3-04 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1617
10-LT-1147 | AI | CBL-0015 | 12 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 5 | 016-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1129
10-FT-1148 | AI | CBL-0015 | 12 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 6 | 016-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1360
10-PT-1149 | AI | CBL-0015 | 12 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 7 | 016-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1655
10-XY-1150 | DO | CBL-0015 | 12 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 8 | 016-CBP-3-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):682
10-TT-1151 | AI | CBL-0015 | 12 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 9 | 016-CBP-3-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1823
|  | CBL-0015 | 12 | 10 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 10 | 016-CBP-3-10 |  |  | Spare
|  | CBL-0015 | 12 | 11 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 11 | 016-CBP-3-11 |  |  | Spare
|  | CBL-0015 | 12 | 12 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-3 | 12 | 016-CBP-3-12 |  |  | Spare
10-PV-1465 | AO | CBL-0053 | 12 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 1 | 016-CBP-4-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):288
10-LS-1466 | DI | CBL-0053 | 12 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 2 | 016-CBP-4-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1167
10-HS-1467 | DI | CBL-0053 | 12 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 3 | 016-CBP-4-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1439
10-PS-1468 | DI | CBL-0053 | 12 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 4 | 016-CBP-4-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1311
10-FV-1469 | AO | CBL-0053 | 12 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 5 | 016-CBP-4-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):237
10-FT-1470 | AI | CBL-0053 | 12 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 6 | 016-CBP-4-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1085
10-FV-1471 | AO | CBL-0053 | 12 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 7 | 016-CBP-4-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):484
10-LS-1472 | DI | CBL-0053 | 12 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 8 | 016-CBP-4-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):496
10-LS-1473 | DI | CBL-0053 | 12 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 9 | 016-CBP-4-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):774
10-TT-1474 | AI | CBL-0053 | 12 | 10 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 10 | 016-CBP-4-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):488
|  | CBL-0053 | 12 | 11 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 11 | 016-CBP-4-11 |  |  | Spare
|  | CBL-0053 | 12 | 12 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-4 | 12 | 016-CBP-4-12 |  |  | Spare
10-HS-1481 | DI | CBL-0055 | 12 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 1 | 016-CBP-5-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1581
10-HS-1482 | DI | CBL-0055 | 12 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 2 | 016-CBP-5-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1650
10-PV-1483 | AO | CBL-0055 | 12 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 3 | 016-CBP-5-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1172
10-PT-1484 | AI | CBL-0055 | 12 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 4 | 016-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1113
10-XV-1485 | DO-SOV | CBL-0055 | 12 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 5 | 016-CBP-5-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1858
|  | CBL-0055 | 12 | 6 | G3 |  | Held (TQ) | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 6 | 016-CBP-5-06 |  |  | Reserved
10-LS-1487 | DI | CBL-0055 | 12 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 7 | 016-CBP-5-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):617
10-XY-1488 | DO | CBL-0055 | 12 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 8 | 016-CBP-5-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):162
10-HN-1489 | DO-HORN | CBL-0055 | 12 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 9 | 016-CBP-5-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):307
10-LT-1490 | AI | CBL-0055 | 12 | 10 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 10 | 016-CBP-5-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):856
10-XV-1491 | DO-SOV | CBL-0055 | 12 | 11 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 11 | 016-CBP-5-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):674
|  | CBL-0055 | 12 | 12 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-5 | 12 | 016-CBP-5-12 |  |  | Spare
10-PS-1809 | DI | CBL-0100 | 12 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 1 | 016-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1641
10-FT-1810 | AI | CBL-0100 | 12 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 2 | 016-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):810
10-XV-1811 | DO-SOV | CBL-0100 | 12 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 3 | 016-CBP-6-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1447
10-ZS-1812 | DI | CBL-0100 | 12 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 4 | 016-CBP-6-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):519
10-PS-1813 | DI | CBL-0100 | 12 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 5 | 016-CBP-6-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1442
10-TE-1814 | AI-RTD | CBL-0100 | 12 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 6 | 016-CBP-6-06 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):760
10-FT-1815 | AI | CBL-0100 | 12 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 7 | 016-CBP-6-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1994
10-TE-1816 | AI-RTD | CBL-0100 | 12 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 8 | 016-CBP-6-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):992
10-LT-1817 | AI | CBL-0100 | 12 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 9 | 016-CBP-6-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1048
|  | CBL-0100 | 12 | 10 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 10 | 016-CBP-6-10 |  |  | Spare
|  | CBL-0100 | 12 | 11 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 11 | 016-CBP-6-11 |  |  | Spare
|  | CBL-0100 | 12 | 12 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-6 | 12 | 016-CBP-6-12 |  |  | Spare
10-HN-2161 | DO-HORN | CBL-0135 | 12 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 1 | 016-CBP-7-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1658
10-FT-2162 | AI | CBL-0135 | 12 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 2 | 016-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):965
10-HY-2163 | DO | CBL-0135 | 12 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 3 | 016-CBP-7-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1643
10-PS-2164 | DI | CBL-0135 | 12 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 4 | 016-CBP-7-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1616
10-PS-2165 | DI | CBL-0135 | 12 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 5 | 016-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):470
10-ZS-2166 | DI | CBL-0135 | 12 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 6 | 016-CBP-7-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):555
10-PT-2167 | AI | CBL-0135 | 12 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 7 | 016-CBP-7-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1191
10-LT-2168 | AI | CBL-0135 | 12 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 8 | 016-CBP-7-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):95
10-MY-2169 | DO-RELAY | CBL-0135 | 12 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 9 | 016-CBP-7-09 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):465
10-LV-2170 | AO | CBL-0135 | 12 | 10 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 10 | 016-CBP-7-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1186
|  | CBL-0135 | 12 | 11 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 11 | 016-CBP-7-11 |  |  | Spare
|  | CBL-0135 | 12 | 12 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-7 | 12 | 016-CBP-7-12 |  |  | Spare
10-XV-2568 | DO-SOV | CBL-0184 | 12 | 1 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 1 | 016-CBP-8-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):688
10-TT-2569 | AI | CBL-0184 | 12 | 2 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 2 | 016-CBP-8-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):349
10-PS-2570 | DI | CBL-0184 | 12 | 3 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 3 | 016-CBP-8-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):947
10-HY-2571 | DO | CBL-0184 | 12 | 4 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 4 | 016-CBP-8-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1957
10-TT-2572 | AI | CBL-0184 | 12 | 5 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 5 | 016-CBP-8-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):473
10-LT-2573 | AI | CBL-0184 | 12 | 6 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 6 | 016-CBP-8-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1115
10-LS-2574 | DI | CBL-0184 | 12 | 7 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 7 | 016-CBP-8-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1322
10-ZS-2575 | DI | CBL-0184 | 12 | 8 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 8 | 016-CBP-8-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1601
10-LS-2576 | DI | CBL-0184 | 12 | 9 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 9 | 016-CBP-8-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):733
10-FT-2577 | AI | CBL-0184 | 12 | 10 | G3 |  | Signal | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 10 | 016-CBP-8-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1341
|  | CBL-0184 | 12 | 11 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 11 | 016-CBP-8-11 |  |  | Spare
|  | CBL-0184 | 12 | 12 | G3 |  | Spare pair | AR1CTL10001 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100016 | 016-CBP-8 | 12 | 016-CBP-8-12 |  |  | Spare
10-PT-1492 | AI | CBL-0056 | 6 | 1 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 1 | 017-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):952
10-PS-1493 | DI | CBL-0056 | 6 | 2 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 2 | 017-CBP-1-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):529
10-LS-1494 | DI | CBL-0056 | 6 | 3 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 3 | 017-CBP-1-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1205
10-HY-1495 | DO | CBL-0056 | 6 | 4 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 4 | 017-CBP-1-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):10
10-ZS-1496 | DI | CBL-0056 | 6 | 5 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 5 | 017-CBP-1-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1973
10-PV-1497 | AO | CBL-0056 | 6 | 6 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 6 | 017-CBP-1-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):939
10-LS-1657 | DI | CBL-0080 | 6 | 1 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 7 | 017-CBP-1-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):82
10-PT-1658 | AI | CBL-0080 | 6 | 2 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 8 | 017-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):295
10-HS-1659 | DI | CBL-0080 | 6 | 3 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 9 | 017-CBP-1-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1560
10-HY-1660 | DO | CBL-0080 | 6 | 4 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 10 | 017-CBP-1-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):419
10-XV-1661 | DO-SOV | CBL-0080 | 6 | 5 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 11 | 017-CBP-1-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):103
|  | CBL-0080 | 6 | 6 | G3 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-1 | 12 | 017-CBP-1-12 |  |  | Spare
10-TT-1737 | AI | CBL-0095 | 6 | 1 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 1 | 017-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1623
10-TT-1738 | AI | CBL-0095 | 6 | 2 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 2 | 017-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1930
10-LT-1739 | AI | CBL-0095 | 6 | 3 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 3 | 017-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1765
10-XV-1740 | DO-SOV | CBL-0095 | 6 | 4 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 4 | 017-CBP-2-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):97
|  | CBL-0095 | 6 | 5 | G3 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 5 | 017-CBP-2-05 |  |  | Spare
|  | CBL-0095 | 6 | 6 | G3 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 6 | 017-CBP-2-06 |  |  | Spare
10-LT-2292 | AI | CBL-0151 | 6 | 1 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 7 | 017-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1770
10-PT-2293 | AI | CBL-0151 | 6 | 2 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 8 | 017-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1260
10-LT-2294 | AI | CBL-0151 | 6 | 3 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 9 | 017-CBP-2-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):79
10-LS-2295 | DI | CBL-0151 | 6 | 4 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 10 | 017-CBP-2-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):679
10-LT-2296 | AI | CBL-0151 | 6 | 5 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 11 | 017-CBP-2-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1942
|  | CBL-0151 | 6 | 6 | G3 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-2 | 12 | 017-CBP-2-12 |  |  | Spare
10-PT-1989B | AI | CBL-0121 | 24 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 1 | 017-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):444
10-LS-1990B | DI | CBL-0121 | 24 | 2 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 2 | 017-CBP-3-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):997
10-HY-1991B | DO | CBL-0121 | 24 | 3 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 3 | 017-CBP-3-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1132
10-TE-1992B | AI-RTD | CBL-0121 | 24 | 4 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 4 | 017-CBP-3-04 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1826
10-HY-1993B | DO | CBL-0121 | 24 | 5 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 5 | 017-CBP-3-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1355
10-LV-1994B | AO | CBL-0121 | 24 | 6 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 6 | 017-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):973
10-HS-1995B | DI | CBL-0121 | 24 | 7 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 7 | 017-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):581
10-TT-1996B | AI | CBL-0121 | 24 | 8 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 8 | 017-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1010
10-LV-1997B | AO | CBL-0121 | 24 | 9 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 9 | 017-CBP-3-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):509
10-LV-1998B | AO | CBL-0121 | 24 | 10 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 10 | 017-CBP-3-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):276
10-LT-1999B | AI | CBL-0121 | 24 | 11 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 11 | 017-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):382
10-FT-2000B | AI | CBL-0121 | 24 | 12 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-3 | 12 | 017-CBP-3-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1168
10-HS-2001B | DI | CBL-0121 | 24 | 13 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 1 | 017-CBP-4-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):560
10-LT-2002B | AI | CBL-0121 | 24 | 14 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 2 | 017-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1651
10-PV-2003B | AO | CBL-0121 | 24 | 15 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 3 | 017-CBP-4-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1103
10-PV-2004B | AO | CBL-0121 | 24 | 16 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 4 | 017-CBP-4-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):749
10-PS-2005B | DI | CBL-0121 | 24 | 17 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 5 | 017-CBP-4-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1728
10-XV-2006B | DO-SOV | CBL-0121 | 24 | 18 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 6 | 017-CBP-4-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1796
10-FV-2007B | AO | CBL-0121 | 24 | 19 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 7 | 017-CBP-4-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1202
10-HS-2008B | DI | CBL-0121 | 24 | 20 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 8 | 017-CBP-4-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):207
10-TT-2009B | AI | CBL-0121 | 24 | 21 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 9 | 017-CBP-4-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1972
10-FV-2010B | AO | CBL-0121 | 24 | 22 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 10 | 017-CBP-4-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):730
|  | CBL-0121 | 24 | 23 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 11 | 017-CBP-4-11 |  |  | Spare
|  | CBL-0121 | 24 | 24 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-05 | AR1CIOC100017 | 017-CBP-4 | 12 | 017-CBP-4-12 |  |  | Spare
10-LS-2110B | DI | CBL-0131 | 24 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 1 | 018-CBP-1-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1932
10-PV-2111B | AO | CBL-0131 | 24 | 2 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 2 | 018-CBP-1-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):976
10-TT-2112B | AI | CBL-0131 | 24 | 3 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 3 | 018-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1837
10-LT-2113B | AI | CBL-0131 | 24 | 4 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 4 | 018-CBP-1-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):577
10-LT-2114B | AI | CBL-0131 | 24 | 5 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 5 | 018-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1156
10-PT-2115B | AI | CBL-0131 | 24 | 6 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 6 | 018-CBP-1-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):15
10-FT-2116B | AI | CBL-0131 | 24 | 7 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 7 | 018-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1669
10-PT-2117B | AI | CBL-0131 | 24 | 8 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 8 | 018-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):756
10-LT-2118B | AI | CBL-0131 | 24 | 9 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 9 | 018-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):131
10-PS-2119B | DI | CBL-0131 | 24 | 10 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 10 | 018-CBP-1-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1325
10-XV-2120B | DO-SOV | CBL-0131 | 24 | 11 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 11 | 018-CBP-1-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):22
10-FV-2121B | AO | CBL-0131 | 24 | 12 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-1 | 12 | 018-CBP-1-12 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1123
10-HS-2122B | DI | CBL-0131 | 24 | 13 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 1 | 018-CBP-2-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1894
10-HN-2123B | DO-HORN | CBL-0131 | 24 | 14 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 2 | 018-CBP-2-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):797
10-LT-2124B | AI | CBL-0131 | 24 | 15 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 3 | 018-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1136
10-LT-2125B | AI | CBL-0131 | 24 | 16 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 4 | 018-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1582
10-TT-2126B | AI | CBL-0131 | 24 | 17 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 5 | 018-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):817
10-LS-2127B | DI | CBL-0131 | 24 | 18 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 6 | 018-CBP-2-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1408
10-LT-2128B | AI | CBL-0131 | 24 | 19 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 7 | 018-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1328
10-FT-2129B | AI | CBL-0131 | 24 | 20 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 8 | 018-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1207
|  | CBL-0131 | 24 | 21 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 9 | 018-CBP-2-09 |  |  | Spare
|  | CBL-0131 | 24 | 22 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 10 | 018-CBP-2-10 |  |  | Spare
|  | CBL-0131 | 24 | 23 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 11 | 018-CBP-2-11 |  |  | Spare
|  | CBL-0131 | 24 | 24 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-2 | 12 | 018-CBP-2-12 |  |  | Spare
10-LT-2488B | AI | CBL-0179 | 24 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 1 | 018-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1697
10-TE-2489B | AI-RTD | CBL-0179 | 24 | 2 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 2 | 018-CBP-3-02 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):262
10-FT-2490B | AI | CBL-0179 | 24 | 3 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 3 | 018-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):741
10-TT-2491B | AI | CBL-0179 | 24 | 4 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 4 | 018-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):405
10-XY-2492B | DO | CBL-0179 | 24 | 5 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 5 | 018-CBP-3-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):252
10-LS-2493B | DI | CBL-0179 | 24 | 6 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 6 | 018-CBP-3-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1691
10-MY-2494B | DO-RELAY | CBL-0179 | 24 | 7 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 7 | 018-CBP-3-07 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):543
10-PT-2495B | AI | CBL-0179 | 24 | 8 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 8 | 018-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):305
10-FT-2496B | AI | CBL-0179 | 24 | 9 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 9 | 018-CBP-3-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):342
10-LV-2497B | AO | CBL-0179 | 24 | 10 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 10 | 018-CBP-3-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1635
10-PS-2498B | DI | CBL-0179 | 24 | 11 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 11 | 018-CBP-3-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):557
10-HS-2499B | DI | CBL-0179 | 24 | 12 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-3 | 12 | 018-CBP-3-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):565
10-LT-2500B | AI | CBL-0179 | 24 | 13 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 1 | 018-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):963
10-LT-2501B | AI | CBL-0179 | 24 | 14 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 2 | 018-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):849
10-PS-2502B | DI | CBL-0179 | 24 | 15 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 3 | 018-CBP-4-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):584
10-HS-2503B | DI | CBL-0179 | 24 | 16 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 4 | 018-CBP-4-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1080
10-TT-2504B | AI | CBL-0179 | 24 | 17 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 5 | 018-CBP-4-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1026
10-TT-2505B | AI | CBL-0179 | 24 | 18 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 6 | 018-CBP-4-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):273
10-PT-2506B | AI | CBL-0179 | 24 | 19 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 7 | 018-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1266
10-HS-2507B | DI | CBL-0179 | 24 | 20 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 8 | 018-CBP-4-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1860
|  | CBL-0179 | 24 | 21 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 9 | 018-CBP-4-09 |  |  | Spare
|  | CBL-0179 | 24 | 22 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 10 | 018-CBP-4-10 |  |  | Spare
|  | CBL-0179 | 24 | 23 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 11 | 018-CBP-4-11 |  |  | Spare
|  | CBL-0179 | 24 | 24 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-4 | 12 | 018-CBP-4-12 |  |  | Spare
10-TT-1638B | AI | CBL-0077 | 12 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 1 | 018-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1990
10-LT-1639B | AI | CBL-0077 | 12 | 2 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 2 | 018-CBP-5-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):469
10-XV-1640B | DO-SOV | CBL-0077 | 12 | 3 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 3 | 018-CBP-5-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1898
10-PT-1641B | AI | CBL-0077 | 12 | 4 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 4 | 018-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1198
10-ZS-1642B | DI | CBL-0077 | 12 | 5 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 5 | 018-CBP-5-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1970
10-FT-1643B | AI | CBL-0077 | 12 | 6 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 6 | 018-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1038
10-LT-1644B | AI | CBL-0077 | 12 | 7 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 7 | 018-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1122
10-LT-1645B | AI | CBL-0077 | 12 | 8 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 8 | 018-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1574
10-PT-1646B | AI | CBL-0077 | 12 | 9 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 9 | 018-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):655
10-FT-1647B | AI | CBL-0077 | 12 | 10 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 10 | 018-CBP-5-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1575
10-LT-1648B | AI | CBL-0077 | 12 | 11 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 11 | 018-CBP-5-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):846
|  | CBL-0077 | 12 | 12 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-5 | 12 | 018-CBP-5-12 |  |  | Spare
10-FT-2252B | AI | CBL-0146 | 12 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 1 | 018-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1107
10-LS-2253B | DI | CBL-0146 | 12 | 2 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 2 | 018-CBP-6-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):522
10-XV-2254B | DO-SOV | CBL-0146 | 12 | 3 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 3 | 018-CBP-6-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1875
10-XY-2255B | DO | CBL-0146 | 12 | 4 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 4 | 018-CBP-6-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):542
10-PS-2256B | DI | CBL-0146 | 12 | 5 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 5 | 018-CBP-6-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):109
10-LT-2257B | AI | CBL-0146 | 12 | 6 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 6 | 018-CBP-6-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):60
10-PT-2258B | AI | CBL-0146 | 12 | 7 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 7 | 018-CBP-6-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):235
10-ZS-2259B | DI | CBL-0146 | 12 | 8 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 8 | 018-CBP-6-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1130
10-TT-2260B | AI | CBL-0146 | 12 | 9 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 9 | 018-CBP-6-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1736
|  | CBL-0146 | 12 | 10 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 10 | 018-CBP-6-10 |  |  | Spare
|  | CBL-0146 | 12 | 11 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 11 | 018-CBP-6-11 |  |  | Spare
|  | CBL-0146 | 12 | 12 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-6 | 12 | 018-CBP-6-12 |  |  | Spare
10-LT-1172B | AI | CBL-0020 | 6 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 1 | 018-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1855
10-XV-1173B | DO-SOV | CBL-0020 | 6 | 2 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 2 | 018-CBP-7-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):591
10-TT-1174B | AI | CBL-0020 | 6 | 3 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 3 | 018-CBP-7-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1564
10-HS-1175B | DI | CBL-0020 | 6 | 4 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 4 | 018-CBP-7-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1559
|  | CBL-0020 | 6 | 5 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 5 | 018-CBP-7-05 |  |  | Spare
|  | CBL-0020 | 6 | 6 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 6 | 018-CBP-7-06 |  |  | Spare
10-XV-2361B | DO-SOV | CBL-0163 | 6 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 7 | 018-CBP-7-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):782
10-HY-2362B | DO | CBL-0163 | 6 | 2 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 8 | 018-CBP-7-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1487
10-LS-2363B | DI | CBL-0163 | 6 | 3 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 9 | 018-CBP-7-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1621
10-HN-2364B | DO-HORN | CBL-0163 | 6 | 4 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 10 | 018-CBP-7-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):451
10-HY-2365B | DO | CBL-0163 | 6 | 5 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 11 | 018-CBP-7-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1464
|  | CBL-0163 | 6 | 6 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-7 | 12 | 018-CBP-7-12 |  |  | Spare
10-XY-1518B | DO | CBL-0059 | 2 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 1 | 018-CBP-8-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1112
10-PS-1519B | DI | CBL-0059 | 2 | 2 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 2 | 018-CBP-8-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1345
10-FT-1735B | AI | CBL-0092 | 2 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 3 | 018-CBP-8-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1662
|  | CBL-0092 | 2 | 2 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 4 | 018-CBP-8-04 |  |  | Spare
10-LT-2303B | AI | CBL-0154 | 2 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 5 | 018-CBP-8-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):452
|  | CBL-0154 | 2 | 2 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 6 | 018-CBP-8-06 |  |  | Spare
10-PT-2623B | AI | CBL-0189 | 2 | 1 | G3 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 7 | 018-CBP-8-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):187
|  | CBL-0189 | 2 | 2 | G3 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 8 | 018-CBP-8-08 |  |  | Spare
10-PS-1861 | DI | CBL-0104 | 2 | 1 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 9 | 018-CBP-8-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):570
10-TT-1862 | AI | CBL-0104 | 2 | 2 | G3 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100018 | 018-CBP-8 | 10 | 018-CBP-8-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1189
10-HS-1206A | DI | CBL-0029 | 24 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 1 | 019-CBP-1-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):361
10-TE-1207A | AI-RTD | CBL-0029 | 24 | 2 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 2 | 019-CBP-1-02 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1584
10-TE-1208A | AI-RTD | CBL-0029 | 24 | 3 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 3 | 019-CBP-1-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):900
10-PS-1209A | DI | CBL-0029 | 24 | 4 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 4 | 019-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):737
10-HN-1210A | DO-HORN | CBL-0029 | 24 | 5 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 5 | 019-CBP-1-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1979
10-LV-1211A | AO | CBL-0029 | 24 | 6 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 6 | 019-CBP-1-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1748
10-PV-1212A | AO | CBL-0029 | 24 | 7 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 7 | 019-CBP-1-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1299
10-PT-1213A | AI | CBL-0029 | 24 | 8 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 8 | 019-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):505
10-PV-1214A | AO | CBL-0029 | 24 | 9 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 9 | 019-CBP-1-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):871
10-PS-1215A | DI | CBL-0029 | 24 | 10 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 10 | 019-CBP-1-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1090
10-PT-1216A | AI | CBL-0029 | 24 | 11 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 11 | 019-CBP-1-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):40
10-ZS-1217A | DI | CBL-0029 | 24 | 12 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-1 | 12 | 019-CBP-1-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):381
10-PV-1218A | AO | CBL-0029 | 24 | 13 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 1 | 019-CBP-2-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):284
10-PT-1219A | AI | CBL-0029 | 24 | 14 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 2 | 019-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1374
10-ZS-1220A | DI | CBL-0029 | 24 | 15 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 3 | 019-CBP-2-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):795
10-LV-1221A | AO | CBL-0029 | 24 | 16 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 4 | 019-CBP-2-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1871
10-XY-1222A | DO | CBL-0029 | 24 | 17 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 5 | 019-CBP-2-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):345
10-XY-1223A | DO | CBL-0029 | 24 | 18 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 6 | 019-CBP-2-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1226
10-LT-1224A | AI | CBL-0029 | 24 | 19 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 7 | 019-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1830
10-HY-1225A | DO | CBL-0029 | 24 | 20 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 8 | 019-CBP-2-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):328
10-XV-1226A | DO-SOV | CBL-0029 | 24 | 21 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 9 | 019-CBP-2-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):351
10-LT-1227A | AI | CBL-0029 | 24 | 22 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 10 | 019-CBP-2-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1853
|  | CBL-0029 | 24 | 23 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 11 | 019-CBP-2-11 |  |  | Spare
|  | CBL-0029 | 24 | 24 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-2 | 12 | 019-CBP-2-12 |  |  | Spare
10-XV-1867A | DO-SOV | CBL-0107 | 24 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 1 | 019-CBP-3-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1228
10-PS-1868A | DI | CBL-0107 | 24 | 2 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 2 | 019-CBP-3-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):250
10-FV-1869A | AO | CBL-0107 | 24 | 3 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 3 | 019-CBP-3-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1495
10-LT-1870A | AI | CBL-0107 | 24 | 4 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 4 | 019-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1788
10-ZS-1871A | DI | CBL-0107 | 24 | 5 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 5 | 019-CBP-3-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):416
10-LT-1872A | AI | CBL-0107 | 24 | 6 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 6 | 019-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1352
10-LS-1873A | DI | CBL-0107 | 24 | 7 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 7 | 019-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1284
10-PT-1874A | AI | CBL-0107 | 24 | 8 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 8 | 019-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1163
10-XY-1875A | DO | CBL-0107 | 24 | 9 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 9 | 019-CBP-3-09 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1273
10-XY-1876A | DO | CBL-0107 | 24 | 10 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 10 | 019-CBP-3-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1608
10-FT-1877A | AI | CBL-0107 | 24 | 11 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 11 | 019-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):55
10-XY-1878A | DO | CBL-0107 | 24 | 12 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-3 | 12 | 019-CBP-3-12 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):701
10-LS-1879A | DI | CBL-0107 | 24 | 13 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 1 | 019-CBP-4-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):93
10-LS-1880A | DI | CBL-0107 | 24 | 14 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 2 | 019-CBP-4-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1105
10-MY-1881A | DO-RELAY | CBL-0107 | 24 | 15 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 3 | 019-CBP-4-03 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):643
10-FT-1882A | AI | CBL-0107 | 24 | 16 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 4 | 019-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1963
10-TE-1883A | AI-RTD | CBL-0107 | 24 | 17 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 5 | 019-CBP-4-05 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1023
10-MY-1884A | DO-RELAY | CBL-0107 | 24 | 18 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 6 | 019-CBP-4-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1412
10-FT-1885A | AI | CBL-0107 | 24 | 19 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 7 | 019-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1852
10-LS-1886A | DI | CBL-0107 | 24 | 20 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 8 | 019-CBP-4-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1110
10-LS-1887A | DI | CBL-0107 | 24 | 21 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 9 | 019-CBP-4-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):486
|  | CBL-0107 | 24 | 22 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 10 | 019-CBP-4-10 |  |  | Spare
|  | CBL-0107 | 24 | 23 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 11 | 019-CBP-4-11 |  |  | Spare
|  | CBL-0107 | 24 | 24 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-4 | 12 | 019-CBP-4-12 |  |  | Spare
10-LT-1072A | AI | CBL-0007 | 12 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 1 | 019-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):455
10-LV-1073A | AO | CBL-0007 | 12 | 2 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 2 | 019-CBP-5-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):549
10-LT-1074A | AI | CBL-0007 | 12 | 3 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 3 | 019-CBP-5-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):297
10-FT-1075A | AI | CBL-0007 | 12 | 4 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 4 | 019-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):646
10-XV-1076A | DO-SOV | CBL-0007 | 12 | 5 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 5 | 019-CBP-5-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1118
10-PT-1077A | AI | CBL-0007 | 12 | 6 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 6 | 019-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):960
10-LT-1078A | AI | CBL-0007 | 12 | 7 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 7 | 019-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1714
10-LV-1079A | AO | CBL-0007 | 12 | 8 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 8 | 019-CBP-5-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):116
10-ZS-1080A | DI | CBL-0007 | 12 | 9 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 9 | 019-CBP-5-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):595
10-PT-1081A | AI | CBL-0007 | 12 | 10 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 10 | 019-CBP-5-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1159
10-ZS-1082A | DI | CBL-0007 | 12 | 11 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 11 | 019-CBP-5-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):792
|  | CBL-0007 | 12 | 12 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-5 | 12 | 019-CBP-5-12 |  |  | Spare
10-PT-1106A | AI | CBL-0011 | 6 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 1 | 019-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1025
10-MY-1107A | DO-RELAY | CBL-0011 | 6 | 2 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 2 | 019-CBP-6-02 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):105
10-XV-1108A | DO-SOV | CBL-0011 | 6 | 3 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 3 | 019-CBP-6-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1149
10-LS-1109A | DI | CBL-0011 | 6 | 4 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 4 | 019-CBP-6-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1512
10-PT-1110A | AI | CBL-0011 | 6 | 5 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 5 | 019-CBP-6-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1992
10-XY-1111A | DO | CBL-0011 | 6 | 6 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 6 | 019-CBP-6-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1834
10-PV-1416A | AO | CBL-0047 | 6 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 7 | 019-CBP-6-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):686
10-TT-1417A | AI | CBL-0047 | 6 | 2 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 8 | 019-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):689
10-PT-1418A | AI | CBL-0047 | 6 | 3 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 9 | 019-CBP-6-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1153
10-LT-1419A | AI | CBL-0047 | 6 | 4 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 10 | 019-CBP-6-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):943
10-FT-1420A | AI | CBL-0047 | 6 | 5 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 11 | 019-CBP-6-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):739
10-ZS-1421A | DI | CBL-0047 | 6 | 6 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-6 | 12 | 019-CBP-6-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):788
10-FT-1634A | AI | CBL-0074 | 6 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 1 | 019-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):714
10-TE-1635A | AI-RTD | CBL-0074 | 6 | 2 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 2 | 019-CBP-7-02 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1128
10-LV-1636A | AO | CBL-0074 | 6 | 3 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 3 | 019-CBP-7-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1664
10-PT-1637A | AI | CBL-0074 | 6 | 4 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 4 | 019-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):830
|  | CBL-0074 | 6 | 5 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 5 | 019-CBP-7-05 |  |  | Spare
|  | CBL-0074 | 6 | 6 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 6 | 019-CBP-7-06 |  |  | Spare
10-HS-1176A | DI | CBL-0021 | 2 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 7 | 019-CBP-7-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1347
10-PS-1177A | DI | CBL-0021 | 2 | 2 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 8 | 019-CBP-7-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):719
10-PS-1183A | DI | CBL-0025 | 2 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 9 | 019-CBP-7-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):243
10-MY-1184A | DO-RELAY | CBL-0025 | 2 | 2 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 10 | 019-CBP-7-10 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1267
10-FT-1394A | AI | CBL-0044 | 2 | 1 | G4 | A | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 11 | 019-CBP-7-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1382
|  | CBL-0044 | 2 | 2 | G4 | A | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100019 | 019-CBP-7 | 12 | 019-CBP-7-12 |  |  | Spare
10-TT-1084 | AI | CBL-0010 | 24 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 1 | 020-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1001
10-TT-1085 | AI | CBL-0010 | 24 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 2 | 020-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):301
10-TT-1086 | AI | CBL-0010 | 24 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 3 | 020-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1571
10-XV-1087 | DO-SOV | CBL-0010 | 24 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 4 | 020-CBP-1-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1211
10-LT-1088 | AI | CBL-0010 | 24 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 5 | 020-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):334
10-XY-1089 | DO | CBL-0010 | 24 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 6 | 020-CBP-1-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):31
10-FT-1090 | AI | CBL-0010 | 24 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 7 | 020-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1739
10-PT-1091 | AI | CBL-0010 | 24 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 8 | 020-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):618
10-XV-1092 | DO-SOV | CBL-0010 | 24 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 9 | 020-CBP-1-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):53
10-XV-1093 | DO-SOV | CBL-0010 | 24 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 10 | 020-CBP-1-10 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1536
10-XY-1094 | DO | CBL-0010 | 24 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 11 | 020-CBP-1-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1282
10-PT-1095 | AI | CBL-0010 | 24 | 12 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-1 | 12 | 020-CBP-1-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1298
10-FT-1096 | AI | CBL-0010 | 24 | 13 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 1 | 020-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):412
10-FT-1097 | AI | CBL-0010 | 24 | 14 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 2 | 020-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1290
10-LT-1098 | AI | CBL-0010 | 24 | 15 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 3 | 020-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1102
10-LS-1099 | DI | CBL-0010 | 24 | 16 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 4 | 020-CBP-2-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1304
10-LS-1100 | DI | CBL-0010 | 24 | 17 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 5 | 020-CBP-2-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):231
10-FT-1101 | AI | CBL-0010 | 24 | 18 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 6 | 020-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):54
10-XV-1102 | DO-SOV | CBL-0010 | 24 | 19 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 7 | 020-CBP-2-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1199
10-PT-1103 | AI | CBL-0010 | 24 | 20 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 8 | 020-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1430
10-TT-1104 | AI | CBL-0010 | 24 | 21 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 9 | 020-CBP-2-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1660
10-FT-1105 | AI | CBL-0010 | 24 | 22 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 10 | 020-CBP-2-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1438
|  | CBL-0010 | 24 | 23 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 11 | 020-CBP-2-11 |  |  | Spare
|  | CBL-0010 | 24 | 24 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-2 | 12 | 020-CBP-2-12 |  |  | Spare
10-MY-1674 | DO-RELAY | CBL-0084 | 24 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 1 | 020-CBP-3-01 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):863
10-HN-1675 | DO-HORN | CBL-0084 | 24 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 2 | 020-CBP-3-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1468
10-ZS-1676 | DI | CBL-0084 | 24 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 3 | 020-CBP-3-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1724
10-TT-1677 | AI | CBL-0084 | 24 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 4 | 020-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):794
10-ZS-1678 | DI | CBL-0084 | 24 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 5 | 020-CBP-3-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):76
10-LV-1679 | AO | CBL-0084 | 24 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 6 | 020-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):826
10-LV-1680 | AO | CBL-0084 | 24 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 7 | 020-CBP-3-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1938
10-LT-1681 | AI | CBL-0084 | 24 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 8 | 020-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):408
10-ZS-1682 | DI | CBL-0084 | 24 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 9 | 020-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1529
10-FV-1683 | AO | CBL-0084 | 24 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 10 | 020-CBP-3-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1553
10-TE-1684 | AI-RTD | CBL-0084 | 24 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 11 | 020-CBP-3-11 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1391
10-PS-1685 | DI | CBL-0084 | 24 | 12 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-3 | 12 | 020-CBP-3-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1245
10-PT-1686 | AI | CBL-0084 | 24 | 13 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 1 | 020-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1239
10-LS-1687 | DI | CBL-0084 | 24 | 14 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 2 | 020-CBP-4-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):552
10-HY-1688 | DO | CBL-0084 | 24 | 15 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 3 | 020-CBP-4-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1254
10-LS-1689 | DI | CBL-0084 | 24 | 16 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 4 | 020-CBP-4-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):497
10-HY-1690 | DO | CBL-0084 | 24 | 17 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 5 | 020-CBP-4-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):709
10-FT-1691 | AI | CBL-0084 | 24 | 18 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 6 | 020-CBP-4-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1563
10-XV-1692 | DO-SOV | CBL-0084 | 24 | 19 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 7 | 020-CBP-4-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):467
|  | CBL-0084 | 24 | 20 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 8 | 020-CBP-4-08 |  |  | Spare
|  | CBL-0084 | 24 | 21 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 9 | 020-CBP-4-09 |  |  | Spare
|  | CBL-0084 | 24 | 22 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 10 | 020-CBP-4-10 |  |  | Spare
|  | CBL-0084 | 24 | 23 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 11 | 020-CBP-4-11 |  |  | Spare
|  | CBL-0084 | 24 | 24 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-4 | 12 | 020-CBP-4-12 |  |  | Spare
10-LV-1788 | AO | CBL-0099 | 24 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 1 | 020-CBP-5-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1908
10-PT-1789 | AI | CBL-0099 | 24 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 2 | 020-CBP-5-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1542
10-ZS-1790 | DI | CBL-0099 | 24 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 3 | 020-CBP-5-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):363
10-PS-1791 | DI | CBL-0099 | 24 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 4 | 020-CBP-5-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):746
10-TT-1792 | AI | CBL-0099 | 24 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 5 | 020-CBP-5-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1141
10-TE-1793 | AI-RTD | CBL-0099 | 24 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 6 | 020-CBP-5-06 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1256
10-FT-1794 | AI | CBL-0099 | 24 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 7 | 020-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1414
10-PT-1795 | AI | CBL-0099 | 24 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 8 | 020-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):958
10-TT-1796 | AI | CBL-0099 | 24 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 9 | 020-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):52
10-LS-1797 | DI | CBL-0099 | 24 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 10 | 020-CBP-5-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1056
10-XV-1798 | DO-SOV | CBL-0099 | 24 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 11 | 020-CBP-5-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):302
10-PS-1799 | DI | CBL-0099 | 24 | 12 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-5 | 12 | 020-CBP-5-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1491
10-PS-1800 | DI | CBL-0099 | 24 | 13 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 1 | 020-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1236
10-PS-1801 | DI | CBL-0099 | 24 | 14 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 2 | 020-CBP-6-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1460
10-LT-1802 | AI | CBL-0099 | 24 | 15 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 3 | 020-CBP-6-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1358
10-LT-1803 | AI | CBL-0099 | 24 | 16 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 4 | 020-CBP-6-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):594
10-HY-1804 | DO | CBL-0099 | 24 | 17 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 5 | 020-CBP-6-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1756
10-LT-1805 | AI | CBL-0099 | 24 | 18 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 6 | 020-CBP-6-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):877
10-XV-1806 | DO-SOV | CBL-0099 | 24 | 19 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 7 | 020-CBP-6-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):890
10-HY-1807 | DO | CBL-0099 | 24 | 20 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 8 | 020-CBP-6-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):784
10-FT-1808 | AI | CBL-0099 | 24 | 21 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 9 | 020-CBP-6-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):376
|  | CBL-0099 | 24 | 22 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 10 | 020-CBP-6-10 |  |  | Spare
|  | CBL-0099 | 24 | 23 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 11 | 020-CBP-6-11 |  |  | Spare
|  | CBL-0099 | 24 | 24 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-6 | 12 | 020-CBP-6-12 |  |  | Spare
10-LT-1818 | AI | CBL-0101 | 24 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 1 | 020-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1410
10-ZS-1819 | DI | CBL-0101 | 24 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 2 | 020-CBP-7-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1939
10-FT-1820 | AI | CBL-0101 | 24 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 3 | 020-CBP-7-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1614
10-LV-1821 | AO | CBL-0101 | 24 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 4 | 020-CBP-7-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):357
10-TT-1822 | AI | CBL-0101 | 24 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 5 | 020-CBP-7-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1629
10-PV-1823 | AO | CBL-0101 | 24 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 6 | 020-CBP-7-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):916
10-PV-1824 | AO | CBL-0101 | 24 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 7 | 020-CBP-7-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):754
10-XV-1825 | DO-SOV | CBL-0101 | 24 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 8 | 020-CBP-7-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):290
10-HY-1826 | DO | CBL-0101 | 24 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 9 | 020-CBP-7-09 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1478
10-ZS-1827 | DI | CBL-0101 | 24 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 10 | 020-CBP-7-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):436
10-PT-1828 | AI | CBL-0101 | 24 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 11 | 020-CBP-7-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1734
10-TT-1829 | AI | CBL-0101 | 24 | 12 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-7 | 12 | 020-CBP-7-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1763
10-TT-1830 | AI | CBL-0101 | 24 | 13 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 1 | 020-CBP-8-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1649
10-TT-1831 | AI | CBL-0101 | 24 | 14 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 2 | 020-CBP-8-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):206
10-HS-1832 | DI | CBL-0101 | 24 | 15 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 3 | 020-CBP-8-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):768
10-PS-1833 | DI | CBL-0101 | 24 | 16 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 4 | 020-CBP-8-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1242
10-LS-1834 | DI | CBL-0101 | 24 | 17 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 5 | 020-CBP-8-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):83
10-XV-1835 | DO-SOV | CBL-0101 | 24 | 18 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 6 | 020-CBP-8-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1286
10-XV-1836 | DO-SOV | CBL-0101 | 24 | 19 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 7 | 020-CBP-8-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1640
10-PT-1837 | AI | CBL-0101 | 24 | 20 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 8 | 020-CBP-8-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):677
10-HS-1838 | DI | CBL-0101 | 24 | 21 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 9 | 020-CBP-8-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):724
|  | CBL-0101 | 24 | 22 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 10 | 020-CBP-8-10 |  |  | Spare
|  | CBL-0101 | 24 | 23 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 11 | 020-CBP-8-11 |  |  | Spare
|  | CBL-0101 | 24 | 24 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100020 | 020-CBP-8 | 12 | 020-CBP-8-12 |  |  | Spare
10-HY-2043 | DO | CBL-0125 | 24 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 1 | 021-CBP-1-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1190
10-PS-2044 | DI | CBL-0125 | 24 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 2 | 021-CBP-1-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):663
10-PT-2045 | AI | CBL-0125 | 24 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 3 | 021-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1717
10-FT-2046 | AI | CBL-0125 | 24 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 4 | 021-CBP-1-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1073
10-TT-2047 | AI | CBL-0125 | 24 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 5 | 021-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1881
10-PV-2048 | AO | CBL-0125 | 24 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 6 | 021-CBP-1-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1984
10-ZS-2049 | DI | CBL-0125 | 24 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 7 | 021-CBP-1-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):622
10-HS-2050 | DI | CBL-0125 | 24 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 8 | 021-CBP-1-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1670
10-FT-2051 | AI | CBL-0125 | 24 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 9 | 021-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):404
10-LT-2052 | AI | CBL-0125 | 24 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 10 | 021-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):693
10-XV-2053 | DO-SOV | CBL-0125 | 24 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 11 | 021-CBP-1-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):379
10-HN-2054 | DO-HORN | CBL-0125 | 24 | 12 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-1 | 12 | 021-CBP-1-12 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1463
10-PT-2055 | AI | CBL-0125 | 24 | 13 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 1 | 021-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1114
10-XV-2056 | DO-SOV | CBL-0125 | 24 | 14 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 2 | 021-CBP-2-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):991
10-PT-2057 | AI | CBL-0125 | 24 | 15 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 3 | 021-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1158
10-LT-2058 | AI | CBL-0125 | 24 | 16 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 4 | 021-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1954
10-PT-2059 | AI | CBL-0125 | 24 | 17 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 5 | 021-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):358
10-FT-2060 | AI | CBL-0125 | 24 | 18 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 6 | 021-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1160
10-FV-2061 | AO | CBL-0125 | 24 | 19 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 7 | 021-CBP-2-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):748
10-PV-2062 | AO | CBL-0125 | 24 | 20 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 8 | 021-CBP-2-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):259
10-XV-2063 | DO-SOV | CBL-0125 | 24 | 21 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 9 | 021-CBP-2-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):772
|  | CBL-0125 | 24 | 22 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 10 | 021-CBP-2-10 |  |  | Spare
|  | CBL-0125 | 24 | 23 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 11 | 021-CBP-2-11 |  |  | Spare
|  | CBL-0125 | 24 | 24 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-2 | 12 | 021-CBP-2-12 |  |  | Spare
10-XV-2073 | DO-SOV | CBL-0127 | 24 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 1 | 021-CBP-3-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1912
10-HS-2074 | DI | CBL-0127 | 24 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 2 | 021-CBP-3-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):330
10-XV-2075 | DO-SOV | CBL-0127 | 24 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 3 | 021-CBP-3-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1987
10-TT-2076 | AI | CBL-0127 | 24 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 4 | 021-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1920
10-TT-2077 | AI | CBL-0127 | 24 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 5 | 021-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):764
10-PV-2078 | AO | CBL-0127 | 24 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 6 | 021-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1406
10-HS-2079 | DI | CBL-0127 | 24 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 7 | 021-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1367
10-XY-2080 | DO | CBL-0127 | 24 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 8 | 021-CBP-3-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1165
10-TT-2081 | AI | CBL-0127 | 24 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 9 | 021-CBP-3-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1744
10-LS-2082 | DI | CBL-0127 | 24 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 10 | 021-CBP-3-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1903
10-ZS-2083 | DI | CBL-0127 | 24 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 11 | 021-CBP-3-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):852
10-TT-2084 | AI | CBL-0127 | 24 | 12 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-3 | 12 | 021-CBP-3-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):944
10-MY-2085 | DO-RELAY | CBL-0127 | 24 | 13 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 1 | 021-CBP-4-01 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):272
10-HN-2086 | DO-HORN | CBL-0127 | 24 | 14 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 2 | 021-CBP-4-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1547
10-FT-2087 | AI | CBL-0127 | 24 | 15 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 3 | 021-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):599
10-FT-2088 | AI | CBL-0127 | 24 | 16 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 4 | 021-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):192
10-HS-2089 | DI | CBL-0127 | 24 | 17 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 5 | 021-CBP-4-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1596
10-LV-2090 | AO | CBL-0127 | 24 | 18 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 6 | 021-CBP-4-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1779
10-XV-2091 | DO-SOV | CBL-0127 | 24 | 19 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 7 | 021-CBP-4-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1929
10-PT-2092 | AI | CBL-0127 | 24 | 20 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 8 | 021-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):723
|  | CBL-0127 | 24 | 21 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 9 | 021-CBP-4-09 |  |  | Spare
|  | CBL-0127 | 24 | 22 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 10 | 021-CBP-4-10 |  |  | Spare
|  | CBL-0127 | 24 | 23 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 11 | 021-CBP-4-11 |  |  | Spare
|  | CBL-0127 | 24 | 24 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-4 | 12 | 021-CBP-4-12 |  |  | Spare
10-FV-1543 | AO | CBL-0068 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 1 | 021-CBP-5-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1009
10-PT-1544 | AI | CBL-0068 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 2 | 021-CBP-5-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):704
10-TT-1545 | AI | CBL-0068 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 3 | 021-CBP-5-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):585
10-ZS-1546 | DI | CBL-0068 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 4 | 021-CBP-5-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1753
10-ZS-1547 | DI | CBL-0068 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 5 | 021-CBP-5-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):141
10-PV-1548 | AO | CBL-0068 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 6 | 021-CBP-5-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):398
10-FT-1549 | AI | CBL-0068 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 7 | 021-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1476
10-XV-1550 | DO-SOV | CBL-0068 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 8 | 021-CBP-5-08 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1251
10-TT-1551 | AI | CBL-0068 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 9 | 021-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):744
|  | CBL-0068 | 12 | 10 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 10 | 021-CBP-5-10 |  |  | Spare
|  | CBL-0068 | 12 | 11 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 11 | 021-CBP-5-11 |  |  | Spare
|  | CBL-0068 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-06 | AR1CIOC100021 | 021-CBP-5 | 12 | 021-CBP-5-12 |  |  | Spare
10-XV-1605 | DO-SOV | CBL-0072 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 1 | 022-CBP-1-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):121
10-PT-1606 | AI | CBL-0072 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 2 | 022-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):348
10-HN-1607 | DO-HORN | CBL-0072 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 3 | 022-CBP-1-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):239
10-ZS-1608 | DI | CBL-0072 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 4 | 022-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1486
10-XV-1609 | DO-SOV | CBL-0072 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 5 | 022-CBP-1-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):374
10-PS-1610 | DI | CBL-0072 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 6 | 022-CBP-1-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1825
10-TT-1611 | AI | CBL-0072 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 7 | 022-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):755
10-HY-1612 | DO | CBL-0072 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 8 | 022-CBP-1-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):457
10-XV-1613 | DO-SOV | CBL-0072 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 9 | 022-CBP-1-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1140
|  | CBL-0072 | 12 | 10 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 10 | 022-CBP-1-10 |  |  | Spare
|  | CBL-0072 | 12 | 11 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 11 | 022-CBP-1-11 |  |  | Spare
|  | CBL-0072 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-1 | 12 | 022-CBP-1-12 |  |  | Spare
10-TE-1662 | AI-RTD | CBL-0081 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 1 | 022-CBP-2-01 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1274
10-PS-1663 | DI | CBL-0081 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 2 | 022-CBP-2-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):695
10-PT-1664 | AI | CBL-0081 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 3 | 022-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1310
10-PT-1665 | AI | CBL-0081 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 4 | 022-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1111
10-PT-1666 | AI | CBL-0081 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 5 | 022-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):920
10-PT-1667 | AI | CBL-0081 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 6 | 022-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):385
10-LT-1668 | AI | CBL-0081 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 7 | 022-CBP-2-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):312
10-HS-1669 | DI | CBL-0081 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 8 | 022-CBP-2-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1180
10-PT-1670 | AI | CBL-0081 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 9 | 022-CBP-2-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1590
10-PT-1671 | AI | CBL-0081 | 12 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 10 | 022-CBP-2-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1185
10-LT-1672 | AI | CBL-0081 | 12 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 11 | 022-CBP-2-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1356
|  | CBL-0081 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-2 | 12 | 022-CBP-2-12 |  |  | Spare
10-FT-1725 | AI | CBL-0090 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 1 | 022-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):839
10-XV-1726 | DO-SOV | CBL-0090 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 2 | 022-CBP-3-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1782
10-XV-1727 | DO-SOV | CBL-0090 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 3 | 022-CBP-3-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):261
10-HS-1728 | DI | CBL-0090 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 4 | 022-CBP-3-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1862
10-TT-1729 | AI | CBL-0090 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 5 | 022-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):609
10-XV-1730 | DO-SOV | CBL-0090 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 6 | 022-CBP-3-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1420
10-HN-1731 | DO-HORN | CBL-0090 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 7 | 022-CBP-3-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):850
10-HY-1732 | DO | CBL-0090 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 8 | 022-CBP-3-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1338
10-LS-1733 | DI | CBL-0090 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 9 | 022-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1201
10-TT-1734 | AI | CBL-0090 | 12 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 10 | 022-CBP-3-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):126
|  | CBL-0090 | 12 | 11 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 11 | 022-CBP-3-11 |  |  | Spare
|  | CBL-0090 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-3 | 12 | 022-CBP-3-12 |  |  | Spare
10-FT-2011 | AI | CBL-0122 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 1 | 022-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):913
10-LS-2012 | DI | CBL-0122 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 2 | 022-CBP-4-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):553
10-MY-2013 | DO-RELAY | CBL-0122 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 3 | 022-CBP-4-03 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):621
10-HS-2014 | DI | CBL-0122 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 4 | 022-CBP-4-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):323
10-HY-2015 | DO | CBL-0122 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 5 | 022-CBP-4-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):102
10-PT-2016 | AI | CBL-0122 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 6 | 022-CBP-4-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):815
10-PT-2017 | AI | CBL-0122 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 7 | 022-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):66
10-PS-2018 | DI | CBL-0122 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 8 | 022-CBP-4-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):19
10-FT-2019 | AI | CBL-0122 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 9 | 022-CBP-4-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):988
|  | CBL-0122 | 12 | 10 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 10 | 022-CBP-4-10 |  |  | Spare
|  | CBL-0122 | 12 | 11 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 11 | 022-CBP-4-11 |  |  | Spare
|  | CBL-0122 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-4 | 12 | 022-CBP-4-12 |  |  | Spare
10-TT-2099 | AI | CBL-0129 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 1 | 022-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1363
10-TT-2100 | AI | CBL-0129 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 2 | 022-CBP-5-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1003
10-FT-2101 | AI | CBL-0129 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 3 | 022-CBP-5-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):164
10-HS-2102 | DI | CBL-0129 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 4 | 022-CBP-5-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1612
10-LT-2103 | AI | CBL-0129 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 5 | 022-CBP-5-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):228
10-TT-2104 | AI | CBL-0129 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 6 | 022-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):517
10-XV-2105 | DO-SOV | CBL-0129 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 7 | 022-CBP-5-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):344
10-TT-2106 | AI | CBL-0129 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 8 | 022-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1195
10-XV-2107 | DO-SOV | CBL-0129 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 9 | 022-CBP-5-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1959
10-HS-2108 | DI | CBL-0129 | 12 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 10 | 022-CBP-5-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):190
10-XV-2109 | DO-SOV | CBL-0129 | 12 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 11 | 022-CBP-5-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1630
|  | CBL-0129 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-5 | 12 | 022-CBP-5-12 |  |  | Spare
10-HS-2182 | DI | CBL-0137 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 1 | 022-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):776
10-HY-2183 | DO | CBL-0137 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 2 | 022-CBP-6-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1257
10-MY-2184 | DO-RELAY | CBL-0137 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 3 | 022-CBP-6-03 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):648
10-PT-2185 | AI | CBL-0137 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 4 | 022-CBP-6-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1710
10-FT-2186 | AI | CBL-0137 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 5 | 022-CBP-6-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):425
10-LV-2187 | AO | CBL-0137 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 6 | 022-CBP-6-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):535
10-PV-2188 | AO | CBL-0137 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 7 | 022-CBP-6-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):73
10-LT-2189 | AI | CBL-0137 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 8 | 022-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):666
10-HS-2190 | DI | CBL-0137 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 9 | 022-CBP-6-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):615
|  | CBL-0137 | 12 | 10 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 10 | 022-CBP-6-10 |  |  | Spare
|  | CBL-0137 | 12 | 11 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 11 | 022-CBP-6-11 |  |  | Spare
|  | CBL-0137 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-6 | 12 | 022-CBP-6-12 |  |  | Spare
10-PV-2217 | AO | CBL-0140 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 1 | 022-CBP-7-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):955
10-FV-2218 | AO | CBL-0140 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 2 | 022-CBP-7-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1449
10-XV-2219 | DO-SOV | CBL-0140 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 3 | 022-CBP-7-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):242
10-HS-2220 | DI | CBL-0140 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 4 | 022-CBP-7-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1928
10-PT-2221 | AI | CBL-0140 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 5 | 022-CBP-7-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):635
10-TE-2222 | AI-RTD | CBL-0140 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 6 | 022-CBP-7-06 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1752
10-ZS-2223 | DI | CBL-0140 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 7 | 022-CBP-7-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1500
10-ZS-2224 | DI | CBL-0140 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 8 | 022-CBP-7-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):300
10-PT-2225 | AI | CBL-0140 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 9 | 022-CBP-7-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1921
10-PT-2226 | AI | CBL-0140 | 12 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 10 | 022-CBP-7-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1485
|  | CBL-0140 | 12 | 11 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 11 | 022-CBP-7-11 |  |  | Spare
|  | CBL-0140 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-7 | 12 | 022-CBP-7-12 |  |  | Spare
10-XV-2391 | DO-SOV | CBL-0170 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 1 | 022-CBP-8-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):631
10-HN-2392 | DO-HORN | CBL-0170 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 2 | 022-CBP-8-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1119
10-HY-2393 | DO | CBL-0170 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 3 | 022-CBP-8-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1721
10-LV-2394 | AO | CBL-0170 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 4 | 022-CBP-8-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1477
10-TT-2395 | AI | CBL-0170 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 5 | 022-CBP-8-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):644
10-FT-2396 | AI | CBL-0170 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 6 | 022-CBP-8-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):697
10-PT-2397 | AI | CBL-0170 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 7 | 022-CBP-8-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):949
10-TE-2398 | AI-RTD | CBL-0170 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 8 | 022-CBP-8-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):367
10-TT-2399 | AI | CBL-0170 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 9 | 022-CBP-8-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):84
10-LS-2400 | DI | CBL-0170 | 12 | 10 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 10 | 022-CBP-8-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1443
10-FT-2401 | AI | CBL-0170 | 12 | 11 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 11 | 022-CBP-8-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):281
|  | CBL-0170 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100022 | 022-CBP-8 | 12 | 022-CBP-8-12 |  |  | Spare
10-XV-2440 | DO-SOV | CBL-0175 | 12 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 1 | 023-CBP-1-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1253
10-FT-2441 | AI | CBL-0175 | 12 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 2 | 023-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):12
10-LS-2442 | DI | CBL-0175 | 12 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 3 | 023-CBP-1-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1889
10-XV-2443 | DO-SOV | CBL-0175 | 12 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 4 | 023-CBP-1-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1805
10-TT-2444 | AI | CBL-0175 | 12 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 5 | 023-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):630
10-FT-2445 | AI | CBL-0175 | 12 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 6 | 023-CBP-1-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1178
10-FT-2446 | AI | CBL-0175 | 12 | 7 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 7 | 023-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1832
10-LV-2447 | AO | CBL-0175 | 12 | 8 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 8 | 023-CBP-1-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1396
10-PT-2448 | AI | CBL-0175 | 12 | 9 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 9 | 023-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):44
|  | CBL-0175 | 12 | 10 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 10 | 023-CBP-1-10 |  |  | Spare
|  | CBL-0175 | 12 | 11 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 11 | 023-CBP-1-11 |  |  | Spare
|  | CBL-0175 | 12 | 12 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-1 | 12 | 023-CBP-1-12 |  |  | Spare
10-PT-1651 | AI | CBL-0079 | 6 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 1 | 023-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1482
10-FV-1652 | AO | CBL-0079 | 6 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 2 | 023-CBP-2-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):226
10-LV-1653 | AO | CBL-0079 | 6 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 3 | 023-CBP-2-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):460
10-MY-1654 | DO-RELAY | CBL-0079 | 6 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 4 | 023-CBP-2-04 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1133
10-PS-1655 | DI | CBL-0079 | 6 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 5 | 023-CBP-2-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1012
10-ZS-1656 | DI | CBL-0079 | 6 | 6 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 6 | 023-CBP-2-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):337
10-PS-2020 | DI | CBL-0123 | 6 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 7 | 023-CBP-2-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):787
10-HY-2021 | DO | CBL-0123 | 6 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 8 | 023-CBP-2-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1407
10-ZS-2022 | DI | CBL-0123 | 6 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 9 | 023-CBP-2-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):790
10-LV-2023 | AO | CBL-0123 | 6 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 10 | 023-CBP-2-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1346
|  | CBL-0123 | 6 | 5 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 11 | 023-CBP-2-11 |  |  | Spare
|  | CBL-0123 | 6 | 6 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-2 | 12 | 023-CBP-2-12 |  |  | Spare
10-XV-2287 | DO-SOV | CBL-0150 | 6 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 1 | 023-CBP-3-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1145
10-XV-2288 | DO-SOV | CBL-0150 | 6 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 2 | 023-CBP-3-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1173
10-LT-2289 | AI | CBL-0150 | 6 | 3 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 3 | 023-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):407
10-MY-2290 | DO-RELAY | CBL-0150 | 6 | 4 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 4 | 023-CBP-3-04 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1083
10-XV-2291 | DO-SOV | CBL-0150 | 6 | 5 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 5 | 023-CBP-3-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1638
|  | CBL-0150 | 6 | 6 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 6 | 023-CBP-3-06 |  |  | Spare
10-PT-1649 | AI | CBL-0078 | 2 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 7 | 023-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1781
10-PV-1650 | AO | CBL-0078 | 2 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 8 | 023-CBP-3-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):703
10-TE-1704 | AI-RTD | CBL-0087 | 2 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 9 | 023-CBP-3-09 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):196
|  | CBL-0087 | 2 | 2 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 10 | 023-CBP-3-10 |  |  | Spare
10-PT-1839 | AI | CBL-0102 | 2 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 11 | 023-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):260
10-PS-1840 | DI | CBL-0102 | 2 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-3 | 12 | 023-CBP-3-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):171
10-HS-1928 | DI | CBL-0114 | 2 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-4 | 1 | 023-CBP-4-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):25
10-LT-1929 | AI | CBL-0114 | 2 | 2 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-4 | 2 | 023-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):531
10-TT-2313 | AI | CBL-0156 | 2 | 1 | G4 |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-4 | 3 | 023-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):168
|  | CBL-0156 | 2 | 2 | G4 |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-4 | 4 | 023-CBP-4-04 |  |  | Spare
10-HS-1206B | DI | CBL-0030 | 24 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 1 | 023-CBP-5-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):4
10-TE-1207B | AI-RTD | CBL-0030 | 24 | 2 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 2 | 023-CBP-5-02 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1344
10-TE-1208B | AI-RTD | CBL-0030 | 24 | 3 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 3 | 023-CBP-5-03 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1499
10-PS-1209B | DI | CBL-0030 | 24 | 4 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 4 | 023-CBP-5-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1339
10-HN-1210B | DO-HORN | CBL-0030 | 24 | 5 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 5 | 023-CBP-5-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):950
10-LV-1211B | AO | CBL-0030 | 24 | 6 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 6 | 023-CBP-5-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):50
10-PV-1212B | AO | CBL-0030 | 24 | 7 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 7 | 023-CBP-5-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1232
10-PT-1213B | AI | CBL-0030 | 24 | 8 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 8 | 023-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1265
10-PV-1214B | AO | CBL-0030 | 24 | 9 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 9 | 023-CBP-5-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1815
10-PS-1215B | DI | CBL-0030 | 24 | 10 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 10 | 023-CBP-5-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1851
10-PT-1216B | AI | CBL-0030 | 24 | 11 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 11 | 023-CBP-5-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):732
10-ZS-1217B | DI | CBL-0030 | 24 | 12 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-5 | 12 | 023-CBP-5-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):366
10-PV-1218B | AO | CBL-0030 | 24 | 13 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 1 | 023-CBP-6-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):43
10-PT-1219B | AI | CBL-0030 | 24 | 14 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 2 | 023-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):492
10-ZS-1220B | DI | CBL-0030 | 24 | 15 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 3 | 023-CBP-6-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1016
10-LV-1221B | AO | CBL-0030 | 24 | 16 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 4 | 023-CBP-6-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):156
10-XY-1222B | DO | CBL-0030 | 24 | 17 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 5 | 023-CBP-6-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):578
10-XY-1223B | DO | CBL-0030 | 24 | 18 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 6 | 023-CBP-6-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1446
10-LT-1224B | AI | CBL-0030 | 24 | 19 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 7 | 023-CBP-6-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):533
10-HY-1225B | DO | CBL-0030 | 24 | 20 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 8 | 023-CBP-6-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):652
10-XV-1226B | DO-SOV | CBL-0030 | 24 | 21 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 9 | 023-CBP-6-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1707
10-LT-1227B | AI | CBL-0030 | 24 | 22 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 10 | 023-CBP-6-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1262
|  | CBL-0030 | 24 | 23 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 11 | 023-CBP-6-11 |  |  | Spare
|  | CBL-0030 | 24 | 24 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-6 | 12 | 023-CBP-6-12 |  |  | Spare
10-XV-1867B | DO-SOV | CBL-0108 | 24 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 1 | 023-CBP-7-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):650
10-PS-1868B | DI | CBL-0108 | 24 | 2 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 2 | 023-CBP-7-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):665
10-FV-1869B | AO | CBL-0108 | 24 | 3 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 3 | 023-CBP-7-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1821
10-LT-1870B | AI | CBL-0108 | 24 | 4 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 4 | 023-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1203
10-ZS-1871B | DI | CBL-0108 | 24 | 5 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 5 | 023-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):823
10-LT-1872B | AI | CBL-0108 | 24 | 6 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 6 | 023-CBP-7-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1544
10-LS-1873B | DI | CBL-0108 | 24 | 7 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 7 | 023-CBP-7-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):726
10-PT-1874B | AI | CBL-0108 | 24 | 8 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 8 | 023-CBP-7-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):397
10-XY-1875B | DO | CBL-0108 | 24 | 9 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 9 | 023-CBP-7-09 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):78
10-XY-1876B | DO | CBL-0108 | 24 | 10 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 10 | 023-CBP-7-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1917
10-FT-1877B | AI | CBL-0108 | 24 | 11 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 11 | 023-CBP-7-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):851
10-XY-1878B | DO | CBL-0108 | 24 | 12 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-7 | 12 | 023-CBP-7-12 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):443
10-LS-1879B | DI | CBL-0108 | 24 | 13 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 1 | 023-CBP-8-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1800
10-LS-1880B | DI | CBL-0108 | 24 | 14 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 2 | 023-CBP-8-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1934
10-MY-1881B | DO-RELAY | CBL-0108 | 24 | 15 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 3 | 023-CBP-8-03 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):563
10-FT-1882B | AI | CBL-0108 | 24 | 16 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 4 | 023-CBP-8-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1743
10-TE-1883B | AI-RTD | CBL-0108 | 24 | 17 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 5 | 023-CBP-8-05 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):217
10-MY-1884B | DO-RELAY | CBL-0108 | 24 | 18 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 6 | 023-CBP-8-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1415
10-FT-1885B | AI | CBL-0108 | 24 | 19 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 7 | 023-CBP-8-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1278
10-LS-1886B | DI | CBL-0108 | 24 | 20 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 8 | 023-CBP-8-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1737
10-LS-1887B | DI | CBL-0108 | 24 | 21 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 9 | 023-CBP-8-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1051
|  | CBL-0108 | 24 | 22 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 10 | 023-CBP-8-10 |  |  | Spare
|  | CBL-0108 | 24 | 23 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 11 | 023-CBP-8-11 |  |  | Spare
|  | CBL-0108 | 24 | 24 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100023 | 023-CBP-8 | 12 | 023-CBP-8-12 |  |  | Spare
10-LT-1072B | AI | CBL-0008 | 12 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 1 | 024-CBP-1-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):321
10-LV-1073B | AO | CBL-0008 | 12 | 2 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 2 | 024-CBP-1-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1297
10-LT-1074B | AI | CBL-0008 | 12 | 3 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 3 | 024-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1558
10-FT-1075B | AI | CBL-0008 | 12 | 4 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 4 | 024-CBP-1-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):556
10-XV-1076B | DO-SOV | CBL-0008 | 12 | 5 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 5 | 024-CBP-1-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1373
10-PT-1077B | AI | CBL-0008 | 12 | 6 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 6 | 024-CBP-1-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1854
10-LT-1078B | AI | CBL-0008 | 12 | 7 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 7 | 024-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1161
10-LV-1079B | AO | CBL-0008 | 12 | 8 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 8 | 024-CBP-1-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):282
10-ZS-1080B | DI | CBL-0008 | 12 | 9 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 9 | 024-CBP-1-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):889
10-PT-1081B | AI | CBL-0008 | 12 | 10 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 10 | 024-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1706
10-ZS-1082B | DI | CBL-0008 | 12 | 11 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 11 | 024-CBP-1-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):459
|  | CBL-0008 | 12 | 12 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-1 | 12 | 024-CBP-1-12 |  |  | Spare
10-PT-1106B | AI | CBL-0012 | 6 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 1 | 024-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):736
10-MY-1107B | DO-RELAY | CBL-0012 | 6 | 2 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 2 | 024-CBP-2-02 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1305
10-XV-1108B | DO-SOV | CBL-0012 | 6 | 3 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 3 | 024-CBP-2-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):317
10-LS-1109B | DI | CBL-0012 | 6 | 4 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 4 | 024-CBP-2-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1000
10-PT-1110B | AI | CBL-0012 | 6 | 5 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 5 | 024-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):587
10-XY-1111B | DO | CBL-0012 | 6 | 6 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 6 | 024-CBP-2-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):742
10-PV-1416B | AO | CBL-0048 | 6 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 7 | 024-CBP-2-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):734
10-TT-1417B | AI | CBL-0048 | 6 | 2 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 8 | 024-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1937
10-PT-1418B | AI | CBL-0048 | 6 | 3 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 9 | 024-CBP-2-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):885
10-LT-1419B | AI | CBL-0048 | 6 | 4 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 10 | 024-CBP-2-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1540
10-FT-1420B | AI | CBL-0048 | 6 | 5 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 11 | 024-CBP-2-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1332
10-ZS-1421B | DI | CBL-0048 | 6 | 6 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-2 | 12 | 024-CBP-2-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1469
10-FT-1634B | AI | CBL-0075 | 6 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 1 | 024-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1505
10-TE-1635B | AI-RTD | CBL-0075 | 6 | 2 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 2 | 024-CBP-3-02 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1134
10-LV-1636B | AO | CBL-0075 | 6 | 3 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 3 | 024-CBP-3-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):240
10-PT-1637B | AI | CBL-0075 | 6 | 4 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 4 | 024-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):692
|  | CBL-0075 | 6 | 5 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 5 | 024-CBP-3-05 |  |  | Spare
|  | CBL-0075 | 6 | 6 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 6 | 024-CBP-3-06 |  |  | Spare
10-HS-1176B | DI | CBL-0022 | 2 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 7 | 024-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):822
10-PS-1177B | DI | CBL-0022 | 2 | 2 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 8 | 024-CBP-3-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1538
10-PS-1183B | DI | CBL-0026 | 2 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 9 | 024-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1543
10-MY-1184B | DO-RELAY | CBL-0026 | 2 | 2 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 10 | 024-CBP-3-10 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):702
10-FT-1394B | AI | CBL-0045 | 2 | 1 | G4 | B | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 11 | 024-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1981
|  | CBL-0045 | 2 | 2 | G4 | B | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100024 | 024-CBP-3 | 12 | 024-CBP-3-12 |  |  | Spare
10-HY-1053 | DO | CBL-0006 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 1 | 025-CBP-1-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1244
10-PT-1054 | AI | CBL-0006 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 2 | 025-CBP-1-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):626
10-XY-1055 | DO | CBL-0006 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 3 | 025-CBP-1-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1759
10-PT-1056 | AI | CBL-0006 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 4 | 025-CBP-1-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1015
10-LT-1057 | AI | CBL-0006 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 5 | 025-CBP-1-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):336
10-ZS-1058 | DI | CBL-0006 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 6 | 025-CBP-1-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1276
10-PV-1059 | AO | CBL-0006 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 7 | 025-CBP-1-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):978
10-LV-1060 | AO | CBL-0006 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 8 | 025-CBP-1-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1261
10-LV-1061 | AO | CBL-0006 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 9 | 025-CBP-1-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1214
10-HS-1062 | DI | CBL-0006 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 10 | 025-CBP-1-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1598
10-LT-1063 | AI | CBL-0006 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 11 | 025-CBP-1-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1384
10-ZS-1064 | DI | CBL-0006 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-1 | 12 | 025-CBP-1-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1089
10-LT-1065 | AI | CBL-0006 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 1 | 025-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):710
10-XV-1066 | DO-SOV | CBL-0006 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 2 | 025-CBP-2-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):994
10-MY-1067 | DO-RELAY | CBL-0006 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 3 | 025-CBP-2-03 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):203
10-XY-1068 | DO | CBL-0006 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 4 | 025-CBP-2-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):902
10-TT-1069 | AI | CBL-0006 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 5 | 025-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1870
10-FT-1070 | AI | CBL-0006 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 6 | 025-CBP-2-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):803
10-PS-1071 | DI | CBL-0006 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 7 | 025-CBP-2-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1696
|  | CBL-0006 | 24 | 20 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 8 | 025-CBP-2-08 |  |  | Spare
|  | CBL-0006 | 24 | 21 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 9 | 025-CBP-2-09 |  |  | Spare
|  | CBL-0006 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 10 | 025-CBP-2-10 |  |  | Spare
|  | CBL-0006 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 11 | 025-CBP-2-11 |  |  | Spare
|  | CBL-0006 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-2 | 12 | 025-CBP-2-12 |  |  | Spare
10-XV-1306 | DO-SOV | CBL-0038 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 1 | 025-CBP-3-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1516
10-LT-1307 | AI | CBL-0038 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 2 | 025-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):974
10-LT-1308 | AI | CBL-0038 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 3 | 025-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1269
10-PT-1309 | AI | CBL-0038 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 4 | 025-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):165
10-XV-1310 | DO-SOV | CBL-0038 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 5 | 025-CBP-3-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):831
10-LV-1311 | AO | CBL-0038 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 6 | 025-CBP-3-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1761
10-LV-1312 | AO | CBL-0038 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 7 | 025-CBP-3-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):403
10-XY-1313 | DO | CBL-0038 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 8 | 025-CBP-3-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):49
10-XV-1314 | DO-SOV | CBL-0038 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 9 | 025-CBP-3-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1071
10-FT-1315 | AI | CBL-0038 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 10 | 025-CBP-3-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1127
10-ZS-1316 | DI | CBL-0038 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 11 | 025-CBP-3-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):201
10-LT-1317 | AI | CBL-0038 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-3 | 12 | 025-CBP-3-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):801
10-PS-1318 | DI | CBL-0038 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 1 | 025-CBP-4-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1713
10-MY-1319 | DO-RELAY | CBL-0038 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 2 | 025-CBP-4-02 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):954
10-TT-1320 | AI | CBL-0038 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 3 | 025-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):987
10-HS-1321 | DI | CBL-0038 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 4 | 025-CBP-4-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1397
10-XV-1322 | DO-SOV | CBL-0038 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 5 | 025-CBP-4-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):824
10-FV-1323 | AO | CBL-0038 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 6 | 025-CBP-4-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):245
10-LS-1324 | DI | CBL-0038 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 7 | 025-CBP-4-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1550
10-LT-1325 | AI | CBL-0038 | 24 | 20 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 8 | 025-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1975
|  | CBL-0038 | 24 | 21 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 9 | 025-CBP-4-09 |  |  | Spare
|  | CBL-0038 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 10 | 025-CBP-4-10 |  |  | Spare
|  | CBL-0038 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 11 | 025-CBP-4-11 |  |  | Spare
|  | CBL-0038 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-4 | 12 | 025-CBP-4-12 |  |  | Spare
10-HN-1347 | DO-HORN | CBL-0040 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 1 | 025-CBP-5-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1783
10-HY-1348 | DO | CBL-0040 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 2 | 025-CBP-5-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):11
10-FV-1349 | AO | CBL-0040 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 3 | 025-CBP-5-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):690
10-PT-1350 | AI | CBL-0040 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 4 | 025-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1627
10-XV-1351 | DO-SOV | CBL-0040 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 5 | 025-CBP-5-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):213
10-FV-1352 | AO | CBL-0040 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 6 | 025-CBP-5-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):778
10-PS-1353 | DI | CBL-0040 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 7 | 025-CBP-5-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):680
10-LT-1354 | AI | CBL-0040 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 8 | 025-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):651
10-XV-1355 | DO-SOV | CBL-0040 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 9 | 025-CBP-5-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):67
10-LV-1356 | AO | CBL-0040 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 10 | 025-CBP-5-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1300
10-FT-1357 | AI | CBL-0040 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 11 | 025-CBP-5-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1040
10-ZS-1358 | DI | CBL-0040 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-5 | 12 | 025-CBP-5-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1950
10-LS-1359 | DI | CBL-0040 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 1 | 025-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):299
10-ZS-1360 | DI | CBL-0040 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 2 | 025-CBP-6-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1171
10-XY-1361 | DO | CBL-0040 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 3 | 025-CBP-6-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):456
10-HY-1362 | DO | CBL-0040 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 4 | 025-CBP-6-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):487
10-HS-1363 | DI | CBL-0040 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 5 | 025-CBP-6-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):901
10-LV-1364 | AO | CBL-0040 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 6 | 025-CBP-6-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1179
10-PS-1365 | DI | CBL-0040 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 7 | 025-CBP-6-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1634
10-TT-1366 | AI | CBL-0040 | 24 | 20 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 8 | 025-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):914
10-TT-1367 | AI | CBL-0040 | 24 | 21 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 9 | 025-CBP-6-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1652
10-LT-1368 | AI | CBL-0040 | 24 | 22 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 10 | 025-CBP-6-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):511
|  | CBL-0040 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 11 | 025-CBP-6-11 |  |  | Spare
|  | CBL-0040 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-6 | 12 | 025-CBP-6-12 |  |  | Spare
10-PT-1395 | AI | CBL-0046 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 1 | 025-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1877
10-ZS-1396 | DI | CBL-0046 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 2 | 025-CBP-7-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1827
10-XV-1397 | DO-SOV | CBL-0046 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 3 | 025-CBP-7-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):985
10-HS-1398 | DI | CBL-0046 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 4 | 025-CBP-7-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1154
10-PS-1399 | DI | CBL-0046 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 5 | 025-CBP-7-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1028
10-PT-1400 | AI | CBL-0046 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 6 | 025-CBP-7-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1059
10-PV-1401 | AO | CBL-0046 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 7 | 025-CBP-7-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1720
10-HS-1402 | DI | CBL-0046 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 8 | 025-CBP-7-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1585
10-TE-1403 | AI-RTD | CBL-0046 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 9 | 025-CBP-7-09 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1755
10-PT-1404 | AI | CBL-0046 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 10 | 025-CBP-7-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):445
10-XY-1405 | DO | CBL-0046 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 11 | 025-CBP-7-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1099
10-XV-1406 | DO-SOV | CBL-0046 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-7 | 12 | 025-CBP-7-12 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):332
10-LV-1407 | AO | CBL-0046 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 1 | 025-CBP-8-01 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):613
10-LV-1408 | AO | CBL-0046 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 2 | 025-CBP-8-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1033
10-XV-1409 | DO-SOV | CBL-0046 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 3 | 025-CBP-8-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1176
10-PS-1410 | DI | CBL-0046 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 4 | 025-CBP-8-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):895
10-TT-1411 | AI | CBL-0046 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 5 | 025-CBP-8-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1814
10-ZS-1412 | DI | CBL-0046 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 6 | 025-CBP-8-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):37
10-LT-1413 | AI | CBL-0046 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 7 | 025-CBP-8-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):783
10-LS-1414 | DI | CBL-0046 | 24 | 20 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 8 | 025-CBP-8-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1523
10-XV-1415 | DO-SOV | CBL-0046 | 24 | 21 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 9 | 025-CBP-8-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1839
|  | CBL-0046 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 10 | 025-CBP-8-10 |  |  | Spare
|  | CBL-0046 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 11 | 025-CBP-8-11 |  |  | Spare
|  | CBL-0046 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-07 | AR1CIOC100025 | 025-CBP-8 | 12 | 025-CBP-8-12 |  |  | Spare
|  | CBL-0073 | 24 | 1 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 1 | 026-CBP-1-01 |  |  | Spare
10-HY-1615 | DO | CBL-0073 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 2 | 026-CBP-1-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):796
10-HS-1616 | DI | CBL-0073 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 3 | 026-CBP-1-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1869
10-FT-1617 | AI | CBL-0073 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 4 | 026-CBP-1-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):117
10-XV-1618 | DO-SOV | CBL-0073 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 5 | 026-CBP-1-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1692
10-ZS-1619 | DI | CBL-0073 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 6 | 026-CBP-1-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1997
10-LT-1620 | AI | CBL-0073 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 7 | 026-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1379
10-PT-1621 | AI | CBL-0073 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 8 | 026-CBP-1-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1645
10-TT-1622 | AI | CBL-0073 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 9 | 026-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):433
10-LT-1623 | AI | CBL-0073 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 10 | 026-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):905
10-XY-1624 | DO | CBL-0073 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 11 | 026-CBP-1-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):897
10-XY-1625 | DO | CBL-0073 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-1 | 12 | 026-CBP-1-12 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1470
10-LS-1626 | DI | CBL-0073 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 1 | 026-CBP-2-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1745
10-HN-1627 | DO-HORN | CBL-0073 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 2 | 026-CBP-2-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):945
10-LT-1628 | AI | CBL-0073 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 3 | 026-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):36
10-XY-1629 | DO | CBL-0073 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 4 | 026-CBP-2-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):832
10-LT-1630 | AI | CBL-0073 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 5 | 026-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):339
10-ZS-1631 | DI | CBL-0073 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 6 | 026-CBP-2-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1628
10-XV-1632 | DO-SOV | CBL-0073 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 7 | 026-CBP-2-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1953
|  | CBL-0073 | 24 | 20 |  |  | Held (TQ) | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 8 | 026-CBP-2-08 |  |  | Reserved
|  | CBL-0073 | 24 | 21 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 9 | 026-CBP-2-09 |  |  | Spare
|  | CBL-0073 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 10 | 026-CBP-2-10 |  |  | Spare
|  | CBL-0073 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 11 | 026-CBP-2-11 |  |  | Spare
|  | CBL-0073 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-2 | 12 | 026-CBP-2-12 |  |  | Spare
10-LT-1746 | AI | CBL-0097 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 1 | 026-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):449
10-XV-1747 | DO-SOV | CBL-0097 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 2 | 026-CBP-3-02 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1068
10-LT-1748 | AI | CBL-0097 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 3 | 026-CBP-3-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):112
10-TT-1749 | AI | CBL-0097 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 4 | 026-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):389
10-PT-1750 | AI | CBL-0097 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 5 | 026-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):528
10-LT-1751 | AI | CBL-0097 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 6 | 026-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1882
10-FV-1752 | AO | CBL-0097 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 7 | 026-CBP-3-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1327
10-FT-1753 | AI | CBL-0097 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 8 | 026-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):525
10-LT-1754 | AI | CBL-0097 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 9 | 026-CBP-3-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):559
10-FT-1755 | AI | CBL-0097 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 10 | 026-CBP-3-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):400
10-TT-1756 | AI | CBL-0097 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 11 | 026-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1820
10-XV-1757 | DO-SOV | CBL-0097 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-3 | 12 | 026-CBP-3-12 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):75
10-PS-1758 | DI | CBL-0097 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 1 | 026-CBP-4-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1383
10-LT-1759 | AI | CBL-0097 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 2 | 026-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):359
10-PT-1760 | AI | CBL-0097 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 3 | 026-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1998
10-FT-1761 | AI | CBL-0097 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 4 | 026-CBP-4-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):264
10-XY-1762 | DO | CBL-0097 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 5 | 026-CBP-4-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1980
10-XY-1763 | DO | CBL-0097 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 6 | 026-CBP-4-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1451
10-LT-1764 | AI | CBL-0097 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 7 | 026-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1101
10-LT-1765 | AI | CBL-0097 | 24 | 20 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 8 | 026-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1798
10-FT-1766 | AI | CBL-0097 | 24 | 21 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 9 | 026-CBP-4-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1790
10-FV-1767 | AO | CBL-0097 | 24 | 22 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 10 | 026-CBP-4-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):968
|  | CBL-0097 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 11 | 026-CBP-4-11 |  |  | Spare
|  | CBL-0097 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-4 | 12 | 026-CBP-4-12 |  |  | Spare
10-HS-1949 | DI | CBL-0117 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 1 | 026-CBP-5-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):827
10-HY-1950 | DO | CBL-0117 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 2 | 026-CBP-5-02 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1139
10-XV-1951 | DO-SOV | CBL-0117 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 3 | 026-CBP-5-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):922
10-HY-1952 | DO | CBL-0117 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 4 | 026-CBP-5-04 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1740
10-FT-1953 | AI | CBL-0117 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 5 | 026-CBP-5-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1787
10-TE-1954 | AI-RTD | CBL-0117 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 6 | 026-CBP-5-06 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):847
10-LS-1955 | DI | CBL-0117 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 7 | 026-CBP-5-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):942
10-ZS-1956 | DI | CBL-0117 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 8 | 026-CBP-5-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1843
10-FV-1957 | AO | CBL-0117 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 9 | 026-CBP-5-09 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):924
10-LS-1958 | DI | CBL-0117 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 10 | 026-CBP-5-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):868
10-FV-1959 | AO | CBL-0117 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 11 | 026-CBP-5-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):181
10-HY-1960 | DO | CBL-0117 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-5 | 12 | 026-CBP-5-12 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1568
10-LT-1961 | AI | CBL-0117 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 1 | 026-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1385
10-PV-1962 | AO | CBL-0117 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 2 | 026-CBP-6-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1319
10-PV-1963 | AO | CBL-0117 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 3 | 026-CBP-6-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):675
10-HS-1964 | DI | CBL-0117 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 4 | 026-CBP-6-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1121
10-PV-1965 | AO | CBL-0117 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 5 | 026-CBP-6-05 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1221
10-PS-1966 | DI | CBL-0117 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 6 | 026-CBP-6-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1600
10-TT-1967 | AI | CBL-0117 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 7 | 026-CBP-6-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1888
10-HS-1968 | DI | CBL-0117 | 24 | 20 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 8 | 026-CBP-6-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1054
|  | CBL-0117 | 24 | 21 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 9 | 026-CBP-6-09 |  |  | Spare
|  | CBL-0117 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 10 | 026-CBP-6-10 |  |  | Spare
|  | CBL-0117 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 11 | 026-CBP-6-11 |  |  | Spare
|  | CBL-0117 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-6 | 12 | 026-CBP-6-12 |  |  | Spare
10-XY-1969 | DO | CBL-0118 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 1 | 026-CBP-7-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):982
10-LS-1970 | DI | CBL-0118 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 2 | 026-CBP-7-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):691
10-XY-1971 | DO | CBL-0118 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 3 | 026-CBP-7-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):414
10-FT-1972 | AI | CBL-0118 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 4 | 026-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):63
10-FT-1973 | AI | CBL-0118 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 5 | 026-CBP-7-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):786
10-LT-1974 | AI | CBL-0118 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 6 | 026-CBP-7-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1567
10-XV-1975 | DO-SOV | CBL-0118 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 7 | 026-CBP-7-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):325
10-FT-1976 | AI | CBL-0118 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 8 | 026-CBP-7-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):270
10-FT-1977 | AI | CBL-0118 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 9 | 026-CBP-7-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1285
10-LT-1978 | AI | CBL-0118 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 10 | 026-CBP-7-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1436
10-PT-1979 | AI | CBL-0118 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 11 | 026-CBP-7-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1682
10-LS-1980 | DI | CBL-0118 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-7 | 12 | 026-CBP-7-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1589
10-XV-1981 | DO-SOV | CBL-0118 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 1 | 026-CBP-8-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):545
10-HS-1982 | DI | CBL-0118 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 2 | 026-CBP-8-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1905
10-PT-1983 | AI | CBL-0118 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 3 | 026-CBP-8-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1683
10-HN-1984 | DO-HORN | CBL-0118 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 4 | 026-CBP-8-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1545
10-MY-1985 | DO-RELAY | CBL-0118 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 5 | 026-CBP-8-05 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1731
10-LT-1986 | AI | CBL-0118 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 6 | 026-CBP-8-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):225
10-ZS-1987 | DI | CBL-0118 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 7 | 026-CBP-8-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):106
|  | CBL-0118 | 24 | 20 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 8 | 026-CBP-8-08 |  |  | Spare
|  | CBL-0118 | 24 | 21 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 9 | 026-CBP-8-09 |  |  | Spare
|  | CBL-0118 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 10 | 026-CBP-8-10 |  |  | Spare
|  | CBL-0118 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 11 | 026-CBP-8-11 |  |  | Spare
|  | CBL-0118 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100026 | 026-CBP-8 | 12 | 026-CBP-8-12 |  |  | Spare
10-XV-2196 | DO-SOV | CBL-0139 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 1 | 027-CBP-1-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1530
10-PV-2197 | AO | CBL-0139 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 2 | 027-CBP-1-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1427
10-TT-2198 | AI | CBL-0139 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 3 | 027-CBP-1-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1067
10-XV-2199 | DO-SOV | CBL-0139 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 4 | 027-CBP-1-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1496
10-HS-2200 | DI | CBL-0139 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 5 | 027-CBP-1-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):603
10-XV-2201 | DO-SOV | CBL-0139 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 6 | 027-CBP-1-06 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):340
10-TT-2202 | AI | CBL-0139 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 7 | 027-CBP-1-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1434
10-HY-2203 | DO | CBL-0139 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 8 | 027-CBP-1-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):715
10-PT-2204 | AI | CBL-0139 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 9 | 027-CBP-1-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1586
10-LT-2205 | AI | CBL-0139 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 10 | 027-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):892
10-PS-2206 | DI | CBL-0139 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 11 | 027-CBP-1-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):566
10-XY-2207 | DO | CBL-0139 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-1 | 12 | 027-CBP-1-12 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):142
10-HY-2208 | DO | CBL-0139 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 1 | 027-CBP-2-01 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1944
10-PV-2209 | AO | CBL-0139 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 2 | 027-CBP-2-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1220
10-HY-2210 | DO | CBL-0139 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 3 | 027-CBP-2-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1177
10-FV-2211 | AO | CBL-0139 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 4 | 027-CBP-2-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):526
10-HY-2212 | DO | CBL-0139 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 5 | 027-CBP-2-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1050
10-PS-2213 | DI | CBL-0139 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 6 | 027-CBP-2-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):410
10-XV-2214 | DO-SOV | CBL-0139 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 7 | 027-CBP-2-07 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1624
10-TT-2215 | AI | CBL-0139 | 24 | 20 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 8 | 027-CBP-2-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1773
10-ZS-2216 | DI | CBL-0139 | 24 | 21 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 9 | 027-CBP-2-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1771
|  | CBL-0139 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 10 | 027-CBP-2-10 |  |  | Spare
|  | CBL-0139 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 11 | 027-CBP-2-11 |  |  | Spare
|  | CBL-0139 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-2 | 12 | 027-CBP-2-12 |  |  | Spare
10-PT-2316 | AI | CBL-0158 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 1 | 027-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1292
10-LT-2317 | AI | CBL-0158 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 2 | 027-CBP-3-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1991
10-HY-2318 | DO | CBL-0158 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 3 | 027-CBP-3-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1418
10-LT-2319 | AI | CBL-0158 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 4 | 027-CBP-3-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1613
10-HY-2320 | DO | CBL-0158 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 5 | 027-CBP-3-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):798
10-LT-2321 | AI | CBL-0158 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 6 | 027-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1024
10-ZS-2322 | DI | CBL-0158 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 7 | 027-CBP-3-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1935
10-TT-2323 | AI | CBL-0158 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 8 | 027-CBP-3-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):72
10-LS-2324 | DI | CBL-0158 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 9 | 027-CBP-3-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):458
10-TT-2325 | AI | CBL-0158 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 10 | 027-CBP-3-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):562
10-LT-2326 | AI | CBL-0158 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 11 | 027-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1481
10-FT-2327 | AI | CBL-0158 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-3 | 12 | 027-CBP-3-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):365
10-TT-2328 | AI | CBL-0158 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 1 | 027-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1175
10-HS-2329 | DI | CBL-0158 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 2 | 027-CBP-4-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1751
10-TT-2330 | AI | CBL-0158 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 3 | 027-CBP-4-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1735
10-PV-2331 | AO | CBL-0158 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 4 | 027-CBP-4-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):98
10-TT-2332 | AI | CBL-0158 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 5 | 027-CBP-4-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):47
10-XY-2333 | DO | CBL-0158 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 6 | 027-CBP-4-06 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):294
10-TT-2334 | AI | CBL-0158 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 7 | 027-CBP-4-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1120
|  | CBL-0158 | 24 | 20 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 8 | 027-CBP-4-08 |  |  | Spare
|  | CBL-0158 | 24 | 21 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 9 | 027-CBP-4-09 |  |  | Spare
|  | CBL-0158 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 10 | 027-CBP-4-10 |  |  | Spare
|  | CBL-0158 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 11 | 027-CBP-4-11 |  |  | Spare
|  | CBL-0158 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-4 | 12 | 027-CBP-4-12 |  |  | Spare
10-LS-2449 | DI | CBL-0176 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 1 | 027-CBP-5-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1224
10-MY-2450 | DO-RELAY | CBL-0176 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 2 | 027-CBP-5-02 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1555
10-LT-2451 | AI | CBL-0176 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 3 | 027-CBP-5-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):489
10-MY-2452 | DO-RELAY | CBL-0176 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 4 | 027-CBP-5-04 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1922
10-XV-2453 | DO-SOV | CBL-0176 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 5 | 027-CBP-5-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):9
10-TT-2454 | AI | CBL-0176 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 6 | 027-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1704
10-TT-2455 | AI | CBL-0176 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 7 | 027-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):244
10-PT-2456 | AI | CBL-0176 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 8 | 027-CBP-5-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1522
10-TT-2457 | AI | CBL-0176 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 9 | 027-CBP-5-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):720
10-XY-2458 | DO | CBL-0176 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 10 | 027-CBP-5-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1767
10-PS-2459 | DI | CBL-0176 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 11 | 027-CBP-5-11 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):848
10-HS-2460 | DI | CBL-0176 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-5 | 12 | 027-CBP-5-12 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):520
10-FT-2461 | AI | CBL-0176 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 1 | 027-CBP-6-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1296
10-TE-2462 | AI-RTD | CBL-0176 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 2 | 027-CBP-6-02 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1075
10-FV-2463 | AO | CBL-0176 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 3 | 027-CBP-6-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):880
10-TE-2464 | AI-RTD | CBL-0176 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 4 | 027-CBP-6-04 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1514
10-FT-2465 | AI | CBL-0176 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 5 | 027-CBP-6-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1428
10-ZS-2466 | DI | CBL-0176 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 6 | 027-CBP-6-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1857
10-TE-2467 | AI-RTD | CBL-0176 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 7 | 027-CBP-6-07 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):298
10-LT-2468 | AI | CBL-0176 | 24 | 20 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 8 | 027-CBP-6-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):979
|  | CBL-0176 | 24 | 21 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 9 | 027-CBP-6-09 |  |  | Spare
|  | CBL-0176 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 10 | 027-CBP-6-10 |  |  | Spare
|  | CBL-0176 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 11 | 027-CBP-6-11 |  |  | Spare
|  | CBL-0176 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-6 | 12 | 027-CBP-6-12 |  |  | Spare
10-PT-2469 | AI | CBL-0177 | 24 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 1 | 027-CBP-7-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):573
10-LS-2470 | DI | CBL-0177 | 24 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 2 | 027-CBP-7-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):767
10-FT-2471 | AI | CBL-0177 | 24 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 3 | 027-CBP-7-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):576
10-FV-2472 | AO | CBL-0177 | 24 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 4 | 027-CBP-7-04 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):765
10-TT-2473 | AI | CBL-0177 | 24 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 5 | 027-CBP-7-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1215
10-MY-2474 | DO-RELAY | CBL-0177 | 24 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 6 | 027-CBP-7-06 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1488
10-LV-2475 | AO | CBL-0177 | 24 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 7 | 027-CBP-7-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):215
10-LV-2476 | AO | CBL-0177 | 24 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 8 | 027-CBP-7-08 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):343
10-LS-2477 | DI | CBL-0177 | 24 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 9 | 027-CBP-7-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1549
10-HY-2478 | DO | CBL-0177 | 24 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 10 | 027-CBP-7-10 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):840
10-TT-2479 | AI | CBL-0177 | 24 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 11 | 027-CBP-7-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1615
10-LT-2480 | AI | CBL-0177 | 24 | 12 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-7 | 12 | 027-CBP-7-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1479
10-FT-2481 | AI | CBL-0177 | 24 | 13 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 1 | 027-CBP-8-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1999
10-FV-2482 | AO | CBL-0177 | 24 | 14 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 2 | 027-CBP-8-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1142
10-HS-2483 | DI | CBL-0177 | 24 | 15 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 3 | 027-CBP-8-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1309
10-TT-2484 | AI | CBL-0177 | 24 | 16 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 4 | 027-CBP-8-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):891
10-FT-2485 | AI | CBL-0177 | 24 | 17 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 5 | 027-CBP-8-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1883
10-TT-2486 | AI | CBL-0177 | 24 | 18 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 6 | 027-CBP-8-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1719
10-HY-2487 | DO | CBL-0177 | 24 | 19 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 7 | 027-CBP-8-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):864
|  | CBL-0177 | 24 | 20 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 8 | 027-CBP-8-08 |  |  | Spare
|  | CBL-0177 | 24 | 21 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 9 | 027-CBP-8-09 |  |  | Spare
|  | CBL-0177 | 24 | 22 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 10 | 027-CBP-8-10 |  |  | Spare
|  | CBL-0177 | 24 | 23 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 11 | 027-CBP-8-11 |  |  | Spare
|  | CBL-0177 | 24 | 24 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100027 | 027-CBP-8 | 12 | 027-CBP-8-12 |  |  | Spare
10-ZS-1043 | DI | CBL-0005 | 12 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 1 | 028-CBP-1-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):551
10-MY-1044 | DO-RELAY | CBL-0005 | 12 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 2 | 028-CBP-1-02 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1365
10-LS-1045 | DI | CBL-0005 | 12 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 3 | 028-CBP-1-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):327
10-HS-1046 | DI | CBL-0005 | 12 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 4 | 028-CBP-1-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):698
10-LS-1047 | DI | CBL-0005 | 12 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 5 | 028-CBP-1-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1746
10-HS-1048 | DI | CBL-0005 | 12 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 6 | 028-CBP-1-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):26
10-XY-1049 | DO | CBL-0005 | 12 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 7 | 028-CBP-1-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1255
10-ZS-1050 | DI | CBL-0005 | 12 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 8 | 028-CBP-1-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):501
10-XV-1051 | DO-SOV | CBL-0005 | 12 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 9 | 028-CBP-1-09 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):937
10-PT-1052 | AI | CBL-0005 | 12 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 10 | 028-CBP-1-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):268
|  | CBL-0005 | 12 | 11 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 11 | 028-CBP-1-11 |  |  | Spare
|  | CBL-0005 | 12 | 12 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-1 | 12 | 028-CBP-1-12 |  |  | Spare
10-PT-1112 | AI | CBL-0013 | 12 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 1 | 028-CBP-2-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):172
10-TT-1113 | AI | CBL-0013 | 12 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 2 | 028-CBP-2-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1661
10-TT-1114 | AI | CBL-0013 | 12 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 3 | 028-CBP-2-03 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1029
10-FT-1115 | AI | CBL-0013 | 12 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 4 | 028-CBP-2-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):386
10-PT-1116 | AI | CBL-0013 | 12 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 5 | 028-CBP-2-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1965
10-PS-1117 | DI | CBL-0013 | 12 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 6 | 028-CBP-2-06 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):632
10-HY-1118 | DO | CBL-0013 | 12 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 7 | 028-CBP-2-07 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1644
10-PS-1119 | DI | CBL-0013 | 12 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 8 | 028-CBP-2-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1993
10-FT-1120 | AI | CBL-0013 | 12 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 9 | 028-CBP-2-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1684
10-FV-1121 | AO | CBL-0013 | 12 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 10 | 028-CBP-2-10 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):435
|  | CBL-0013 | 12 | 11 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 11 | 028-CBP-2-11 |  |  | Spare
|  | CBL-0013 | 12 | 12 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-2 | 12 | 028-CBP-2-12 |  |  | Spare
10-PT-1152 | AI | CBL-0016 | 12 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 1 | 028-CBP-3-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):41
10-LV-1153 | AO | CBL-0016 | 12 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 2 | 028-CBP-3-02 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1170
10-HY-1154 | DO | CBL-0016 | 12 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 3 | 028-CBP-3-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1377
10-PS-1155 | DI | CBL-0016 | 12 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 4 | 028-CBP-3-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):946
10-LT-1156 | AI | CBL-0016 | 12 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 5 | 028-CBP-3-05 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):86
10-TT-1157 | AI | CBL-0016 | 12 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 6 | 028-CBP-3-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1671
10-TT-1158 | AI | CBL-0016 | 12 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 7 | 028-CBP-3-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1808
10-TE-1159 | AI-RTD | CBL-0016 | 12 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 8 | 028-CBP-3-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1381
10-LT-1160 | AI | CBL-0016 | 12 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 9 | 028-CBP-3-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1238
10-ZS-1161 | DI | CBL-0016 | 12 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 10 | 028-CBP-3-10 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):137
10-LT-1162 | AI | CBL-0016 | 12 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 11 | 028-CBP-3-11 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):984
|  | CBL-0016 | 12 | 12 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-3 | 12 | 028-CBP-3-12 |  |  | Spare
10-FT-1384 | AI | CBL-0043 | 12 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 1 | 028-CBP-4-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1052
10-FT-1385 | AI | CBL-0043 | 12 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 2 | 028-CBP-4-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1679
10-HY-1386 | DO | CBL-0043 | 12 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 3 | 028-CBP-4-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1055
10-XV-1387 | DO-SOV | CBL-0043 | 12 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 4 | 028-CBP-4-04 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):640
10-MY-1388 | DO-RELAY | CBL-0043 | 12 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 5 | 028-CBP-4-05 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1880
10-LT-1389 | AI | CBL-0043 | 12 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 6 | 028-CBP-4-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):485
10-PV-1390 | AO | CBL-0043 | 12 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 7 | 028-CBP-4-07 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1061
10-LT-1391 | AI | CBL-0043 | 12 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 8 | 028-CBP-4-08 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):471
10-HY-1392 | DO | CBL-0043 | 12 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 9 | 028-CBP-4-09 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1681
10-TT-1393 | AI | CBL-0043 | 12 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 10 | 028-CBP-4-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1106
|  | CBL-0043 | 12 | 11 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 11 | 028-CBP-4-11 |  |  | Spare
|  | CBL-0043 | 12 | 12 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-4 | 12 | 028-CBP-4-12 |  |  | Spare
10-TT-1888 | AI | CBL-0109 | 12 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 1 | 028-CBP-5-01 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):934
10-HS-1889 | DI | CBL-0109 | 12 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 2 | 028-CBP-5-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):70
10-HN-1890 | DO-HORN | CBL-0109 | 12 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 3 | 028-CBP-5-03 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):569
10-TT-1891 | AI | CBL-0109 | 12 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 4 | 028-CBP-5-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):2003
10-ZS-1892 | DI | CBL-0109 | 12 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 5 | 028-CBP-5-05 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1432
10-FT-1893 | AI | CBL-0109 | 12 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 6 | 028-CBP-5-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1392
10-LT-1894 | AI | CBL-0109 | 12 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 7 | 028-CBP-5-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1230
10-TE-1895 | AI-RTD | CBL-0109 | 12 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 8 | 028-CBP-5-08 | RTD CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):23
10-PS-1896 | DI | CBL-0109 | 12 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 9 | 028-CBP-5-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1162
|  | CBL-0109 | 12 | 10 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 10 | 028-CBP-5-10 |  |  | Spare
|  | CBL-0109 | 12 | 11 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 11 | 028-CBP-5-11 |  |  | Spare
|  | CBL-0109 | 12 | 12 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-5 | 12 | 028-CBP-5-12 |  |  | Spare
10-HS-1917 | DI | CBL-0113 | 12 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 1 | 028-CBP-6-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1334
10-FT-1918 | AI | CBL-0113 | 12 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 2 | 028-CBP-6-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1594
10-FV-1919 | AO | CBL-0113 | 12 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 3 | 028-CBP-6-03 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):123
10-ZS-1920 | DI | CBL-0113 | 12 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 4 | 028-CBP-6-04 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):983
10-HY-1921 | DO | CBL-0113 | 12 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 5 | 028-CBP-6-05 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1966
10-LT-1922 | AI | CBL-0113 | 12 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 6 | 028-CBP-6-06 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1897
10-PT-1923 | AI | CBL-0113 | 12 | 7 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 7 | 028-CBP-6-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):364
10-PS-1924 | DI | CBL-0113 | 12 | 8 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 8 | 028-CBP-6-08 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1312
10-PT-1925 | AI | CBL-0113 | 12 | 9 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 9 | 028-CBP-6-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):926
10-TT-1926 | AI | CBL-0113 | 12 | 10 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 10 | 028-CBP-6-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):838
10-PV-1927 | AO | CBL-0113 | 12 | 11 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 11 | 028-CBP-6-11 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):372
|  | CBL-0113 | 12 | 12 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-6 | 12 | 028-CBP-6-12 |  |  | Spare
10-HN-1521 | DO-HORN | CBL-0061 | 6 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 1 | 028-CBP-7-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):306
10-PT-1522 | AI | CBL-0061 | 6 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 2 | 028-CBP-7-02 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):232
10-PS-1523 | DI | CBL-0061 | 6 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 3 | 028-CBP-7-03 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1812
10-PT-1524 | AI | CBL-0061 | 6 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 4 | 028-CBP-7-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1599
10-HN-1525 | DO-HORN | CBL-0061 | 6 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 5 | 028-CBP-7-05 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1445
10-PV-1526 | AO | CBL-0061 | 6 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 6 | 028-CBP-7-06 | AO 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):483
10-ZS-2093 | DI | CBL-0128 | 6 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 7 | 028-CBP-7-07 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):971
10-MY-2094 | DO-RELAY | CBL-0128 | 6 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 8 | 028-CBP-7-08 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1673
10-HS-2095 | DI | CBL-0128 | 6 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 9 | 028-CBP-7-09 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):887
10-MY-2096 | DO-RELAY | CBL-0128 | 6 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 10 | 028-CBP-7-10 | DO 24 V DC High-side CHARM | Relay output | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1891
10-XV-2097 | DO-SOV | CBL-0128 | 6 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 11 | 028-CBP-7-11 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1774
10-TT-2098 | AI | CBL-0128 | 6 | 6 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-7 | 12 | 028-CBP-7-12 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):845
10-HN-2383 | DO-HORN | CBL-0168 | 6 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 1 | 028-CBP-8-01 | DO 24 V DC Isolated CHARM | Fused-injected-power | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1845
10-ZS-2384 | DI | CBL-0168 | 6 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 2 | 028-CBP-8-02 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):315
10-HY-2385 | DO | CBL-0168 | 6 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 3 | 028-CBP-8-03 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):745
10-PT-2386 | AI | CBL-0168 | 6 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 4 | 028-CBP-8-04 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1659
|  | CBL-0168 | 6 | 5 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 5 | 028-CBP-8-05 |  |  | Spare
|  | CBL-0168 | 6 | 6 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 6 | 028-CBP-8-06 |  |  | Spare
10-LT-2618 | AI | CBL-0187 | 6 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 7 | 028-CBP-8-07 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1668
10-XY-2619 | DO | CBL-0187 | 6 | 2 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 8 | 028-CBP-8-08 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1094
10-LT-2620 | AI | CBL-0187 | 6 | 3 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 9 | 028-CBP-8-09 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1525
10-LT-2621 | AI | CBL-0187 | 6 | 4 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 10 | 028-CBP-8-10 | AI 4-20 mA HART CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):941
10-XY-2622 | DO | CBL-0187 | 6 | 5 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 11 | 028-CBP-8-11 | DO 24 V DC High-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1315
|  | CBL-0187 | 6 | 6 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100028 | 028-CBP-8 | 12 | 028-CBP-8-12 |  |  | Spare
10-ZS-1285 | DI | CBL-0036 | 2 | 1 |  |  | Signal | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100029 | 029-CBP-1 | 1 | 029-CBP-1-01 | DI 24 V DC low-side CHARM | Standard | Allocated |  | mdb.xlsx:IO MDB (SYNTHETIC):1258
|  | CBL-0036 | 2 | 2 |  |  | Spare pair | AR1CTL10002 | AR1-DCS-100-01 | AR1-DCM-100-08 | AR1CIOC100029 | 029-CBP-1 | 2 | 029-CBP-1-02 |  |  | Spare
10-HN-1335 | DO-HORN | CBL-0039 |  | 10 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):536
10-HN-1337 | DO-HORN | CBL-0039 |  | 12 | G1 | A | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):1604
10-HS-1330 | DI | CBL-0039 |  | 5 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):91
10-HY-1326 | DO | CBL-0039 |  | 1 | G1 | B | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):712
10-HY-1340 | DO | CBL-0039 |  | 15 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):1760
10-HY-1614 | DO | CBL-0073 |  | 20 |  |  | Signal | [9 empty] | TQ raised | TQ-0004 | mdb.xlsx:IO MDB (SYNTHETIC):1213
10-LS-1327 | DI | CBL-0039 |  | 2 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):293
10-LS-1333 | DI | CBL-0039 |  | 8 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):202
10-LS-1334 | DI | CBL-0039 |  | 9 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):426
10-LS-1339 | DI | CBL-0039 |  | 14 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):1354
10-LS-1341 | DI | CBL-0039 |  | 16 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):320
10-LS-1343 | DI | CBL-0039 |  | 18 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):1844
10-LS-1486 |  | CBL-0055 |  | 6 | G3 |  | Signal | [9 empty] | TQ raised | TQ-0002 | mdb.xlsx:IO MDB (SYNTHETIC):769
10-LT-1328 | AI | CBL-0039 |  | 3 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):658
10-LT-1331 | AI | CBL-0039 |  | 6 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):708
10-LT-1345 | AI | CBL-0039 |  | 20 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):441
10-LT-1595 | DO-SOV | CBL-0133 |  | 19 | G1 | B | Signal | [9 empty] | TQ raised | TQ-0001 | mdb.xlsx:IO MDB (SYNTHETIC):540
10-LT-1595 | AI | CBL-0071 |  | 13 | G2 |  | Signal | [9 empty] | TQ raised | TQ-0001 | mdb.xlsx:IO MDB (SYNTHETIC):1417
10-LT-2128A | PULSE-XYZ | CBL-0130 |  | 19 | G3 | A | Signal | [9 empty] | TQ raised | TQ-0003 | mdb.xlsx:IO MDB (SYNTHETIC):1314
10-LT-2523A | AI | CBL-0180 |  | 25 | G2 | A | Signal | [9 empty] | TQ raised | TQ-0005 | mdb.xlsx:IO MDB (SYNTHETIC):394
10-PS-1342 | DI | CBL-0039 |  | 17 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):110
10-PV-1329 | AO | CBL-0039 |  | 4 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):1403
10-PV-1346 | AO | CBL-0039 |  | 21 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):915
10-PV-1633 | AO | CBL-0073 |  | 20 |  |  | Signal | [9 empty] | TQ raised | TQ-0004 | mdb.xlsx:IO MDB (SYNTHETIC):48
10-TT-1338 | AI | CBL-0039 |  | 13 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):1287
10-XY-1332 | DO | CBL-0039 |  | 7 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):1804
10-XY-1336 | DO | CBL-0039 |  | 11 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):705
10-ZS-1344 | DI | CBL-0039 |  | 19 | G1 |  | Signal | [9 empty] | TQ raised | TQ-0006 | mdb.xlsx:IO MDB (SYNTHETIC):1618

## Cabinet Summary
Marshalling Cabinet | CIOCs | Baseplates used | Empty baseplates (cabinet spare) | Signals | Wired spare pairs | Held for TQ | Free slots on used baseplates | Fill % (signals / cabinet slots) | Fill % (occupied / cabinet slots)
AR1-DCM-100-01 | 4 | 28 | 4 | 281 | 55 | 0 | 0 | 73.2 | 87.5
AR1-DCM-100-02 | 2 | 13 | 19 | 126 | 25 | 1 | 4 | 32.8 | 39.6
AR1-DCM-100-03 | 4 | 28 | 4 | 274 | 61 | 1 | 0 | 71.4 | 87.5
AR1-DCM-100-04 | 3 | 24 | 8 | 222 | 56 | 0 | 10 | 57.8 | 72.4
AR1-DCM-100-05 | 4 | 28 | 4 | 277 | 57 | 2 | 0 | 72.1 | 87.5
AR1-DCM-100-06 | 4 | 28 | 4 | 284 | 50 | 0 | 2 | 74 | 87
AR1-DCM-100-07 | 4 | 27 | 5 | 269 | 47 | 0 | 8 | 70.1 | 82.3
AR1-DCM-100-08 | 4 | 25 | 7 | 241 | 48 | 1 | 10 | 62.8 | 75.5

## TQ List
TQ | Severity | Category | Rule | Message | Tags | Cables | Source rows | Suggested action
TQ-0001 | blocking | data | D-4 | Tag 10-LT-1595 appears 2 times in the MDB | 10-LT-1595 |  | mdb.xlsx:IO MDB (SYNTHETIC):540, mdb.xlsx:IO MDB (SYNTHETIC):1417 | Confirm which row is valid or rename the duplicate
TQ-0002 | blocking | data | D-1 | 10-LS-1486: missing IO type | 10-LS-1486 | CBL-0055 | mdb.xlsx:IO MDB (SYNTHETIC):769 | Correct the MDB row or add a rule for this IO type
TQ-0003 | blocking | hardware | H-* | 10-LT-2128A: IO type 'PULSE-XYZ' has no CHARM/terminal-block rule | 10-LT-2128A | CBL-0130 | mdb.xlsx:IO MDB (SYNTHETIC):1314 | Correct the MDB row or add a rule for this IO type
TQ-0004 | blocking | data | D-5 | Cable CBL-0073 pair 20 is assigned to 2 tags: 10-PV-1633, 10-HY-1614 | 10-PV-1633, 10-HY-1614 | CBL-0073 | mdb.xlsx:IO MDB (SYNTHETIC):48, mdb.xlsx:IO MDB (SYNTHETIC):1213 | Confirm which tag uses this pair
TQ-0005 | blocking | data | D-3 | 10-LT-2523A: pair 25 exceeds the 24-pair size of cable CBL-0180 | 10-LT-2523A | CBL-0180 | mdb.xlsx:IO MDB (SYNTHETIC):394 | Correct the pair number or the cable size
TQ-0006 | blocking | rule-conflict | S-2 | Cable CBL-0039 carries both A and B signals; the cable cannot be kept together and segregated | 10-HS-1330, 10-PS-1342, 10-LS-1333, 10-LS-1327, 10-LS-1341, 10-LS-1334, 10-LT-1345, 10-HN-1335, 10-LT-1328, 10-XY-1336, 10-LT-1331, 10-HY-1326, 10-PV-1346, 10-TT-1338, 10-LS-1339, 10-PV-1329, 10-HN-1337, 10-ZS-1344, 10-HY-1340, 10-XY-1332 | CBL-0039 | mdb.xlsx:IO MDB (SYNTHETIC):91, mdb.xlsx:IO MDB (SYNTHETIC):110, mdb.xlsx:IO MDB (SYNTHETIC):202, mdb.xlsx:IO MDB (SYNTHETIC):293, mdb.xlsx:IO MDB (SYNTHETIC):320, mdb.xlsx:IO MDB (SYNTHETIC):426, mdb.xlsx:IO MDB (SYNTHETIC):441, mdb.xlsx:IO MDB (SYNTHETIC):536, mdb.xlsx:IO MDB (SYNTHETIC):658, mdb.xlsx:IO MDB (SYNTHETIC):705, mdb.xlsx:IO MDB (SYNTHETIC):708, mdb.xlsx:IO MDB (SYNTHETIC):712, mdb.xlsx:IO MDB (SYNTHETIC):915, mdb.xlsx:IO MDB (SYNTHETIC):1287, mdb.xlsx:IO MDB (SYNTHETIC):1354, mdb.xlsx:IO MDB (SYNTHETIC):1403, mdb.xlsx:IO MDB (SYNTHETIC):1604, mdb.xlsx:IO MDB (SYNTHETIC):1618, mdb.xlsx:IO MDB (SYNTHETIC):1760, mdb.xlsx:IO MDB (SYNTHETIC):1804 | Re-route one side to a separate cable

## Rule Check
Rule | Check | Result | Violations | Examples
Q-1 | Every MDB signal is allocated or has a TQ | PASS | 0
D-2 | One signal per CHARM slot (no slot used twice) | PASS | 0
C-1 | Capacity: 12 CHARMs/baseplate, 8 baseplates/CIOC, 4 CIOCs/cabinet | PASS | 0
K-1 | Each cable lands complete, side by side, in pair order | PASS | 0
S-1 | A and B signals never share a CIOC | PASS | 0
G-1 | IO groups isolated and kept in contiguous cabinets | PASS | 0
P-1 | Spare room: required empty baseplates in every cabinet | PASS | 0
H-1..6 | Correct CHARM and terminal block per signal type | PASS | 0
N-1..6 | Names follow the user-defined patterns | PASS | 0
C-2 | Each CIOC has one controller; controller CIOC limit respected | PASS | 0
M-1 | Allocated rows match the MDB (IO type, cable, pair, group, seg) | PASS | 0

## Rule Set
Parameter | Value
name | Default (PS #02 rulebook)
version | 1
charms_per_baseplate | 12
baseplates_per_cioc | 8
ciocs_per_cabinet | 4
max_ciocs_per_controller | 16
controllers_per_system_cabinet | 4
standard_cable_sizes | [2, 6, 12, 24]
allow_cable_straddle | False
multi_baseplate_cables_same_cioc | True
group_isolation_level | cioc
ungrouped_may_share_group_cioc | False
segregation_level | cioc
segregation_values | ['A', 'B']
spare_percent | 10.0
spare_rounding | ceil
block_order | ffd
naming | {'area': 'AR1', 'unit': '100', 'system_cabinet': '{area}-DCS-{unit}-{seq:02d}', 'controller': '{area}CTL{unit}{seq:02d}', 'marshalling_cabinet': '{area}-DCM-{unit}-{seq:02d}', 'cioc': '{area}CIOC{unit}{seq:03d}', 'baseplate': '{cioc_no:03d}-CBP-{n}', 'charm_slot': '{cioc_no:03d}-CBP-{n}-{slot:02d}'}
hardware H-1 | ['AI'] -> AI 4-20 mA HART CHARM / Standard
hardware H-1b | ['AI-RTD'] -> RTD CHARM / Standard
hardware H-2 | ['AO'] -> AO 4-20 mA HART CHARM / Standard
hardware H-3 | ['DI'] -> DI 24 V DC low-side CHARM / Standard
hardware H-4 | ['DO-SOV', 'DO-HORN', 'DO-BEACON', 'DO-SOUNDER', 'DO-ISO'] -> DO 24 V DC Isolated CHARM / Fused-injected-power
hardware H-5 | ['DO'] -> DO 24 V DC High-side CHARM / Standard
hardware H-6 | ['DO-RELAY'] -> DO 24 V DC High-side CHARM / Relay output

## Run Info
Key | Value
tool | SlotSmith 0.1.0
rule set | Default (PS #02 rulebook)
inputs | data/synthetic/mdb.xlsx
note | Generated end-to-end; no hand-editing